## Instructions
2024 Commercial Efficiency Program
Instructions
Instructions for Completing the HVAC Worksheet
The PSEG Long Island HVAC Worksheet gathers data on a customer, their existing AC equipment (if applicable) and their proposed heating and cooling equipment. It automatically calculates the anticipated rebate for the proposed project.
Cells requiring input are shaded with a gray background. Cells with white background are locked for automated population.
To complete the worksheet, follow these simple steps:
| 1. | Enter account, customer, building, and contractor information in the Customer Information tab.
| 2. | Enter the equipment information in the table on the HVAC Worksheet tab.
Enter information from left to right, in order. Equipment Type must be entered before the Size Category, and the Size Category before Sub Code.
|  | • | Enter the information for proposed equipment AND the existing equipment (where applicable).
|  | • | All cells with gray backgrounds in a row must be filled out.
|  | • | All cells with dark gray backgrounds are not applicable to the particular equipment type selected and are to be left blank.
|  | • | Enter only one new / existing combination per row. Use multiple rows for areas with more than one new / existing combination.
| 3. | The Equipment Status cell will evaluate to PASS or FAIL once you enter information. If the cell evaluates to FAIL, then either the existing equipment type does not qualify, the size category does not meet the specified range, or the proposed and/or existing efficiencies do not meet program requirements. Check the input data for accuracy.
| 4. | The rebate will be displayed at the end of each row, and totaled at the top of the page under ‘Total Estimated Rebate.’
| 5. | If the rebate cell is blank, check the inputs to see if all criteria are met. The rebate cell will be blank if the quantity is zero, the size is zero, or if the equipment status cell evaluates to an error.
| 6. | If your project requires more than 25 lines to list all equipment, continue on a second HVAC Worksheet.
As indicated on the application, submit completed worksheet and any other required documents to CEPLI@PSEG.com or upload to the Lead Partner Portal Online Application. Be sure to include the PSEG Long Island account number in the subject line of emails.

## Customer Information
2024 Commercial Efficiency Program
HVAC Rebate Application, Version 3
The Commercial Efficiency Program offers rebates to commercial, industrial, institutional, educational, municipal or multi-family building customers who install qualifying energy efficient equipment. Rebates require pre-approval.
Customer Information
Account No: | [5 empty] | Rate Code:
Account Name: | [5 empty] | Tax ID #:
Facility Address: |  |  |  | City: |  |  | Zip:
Mailing Address: (If different than above) |  |  |  | City: |  |  | Zip:
DBA: |  |  |  |  | Business Phone:
Contact Name/Title: |  |  |  |  | Cell Phone:
E-Mail Address: |  |  |  |  | Fax:
Organization Type: |  | Select… |  |  |  | Building Size (ft2):
Building Type: |  | Select …
Project Type: |  | Select… |  |  | Located in a Disadvantaged Community: |  | Select…
https://www.nyserda.ny.gov/ny/disadvantaged-communities
Rebate Payment Method: |  | Select…
Contractor Information
Contractor Name:
Contractor Address: |  |  |  | City: |  |  | Zip:
Contact Name/Title: |  |  |  | Business Phone:
Tax ID #: |  |  |  | Cell Phone:
E-Mail Address: |  |  |  | Fax:
Rebate
Enter Total Estimated Rebate Amount (Calculated on appropriate worksheet): |  |  | $
*Disclaimer: Terms and conditions are subject to change without notice, including early termination of this promotion. No additional fees apply. The rebate may be issued in the form of a check. PSEG Long Island administers the rebate program on behalf of the Long Island Power Authority, the rebate program sponsor. Please visit https://www.PSEGLINY.com/Efficiency for more details.
Certification Statement: Customer has read, understands and agrees to be bound by the Terms and Conditions set forth herein, and agrees to abide by them. By participating in this program, Customer agrees on behalf of itself and any successor in interest or assignee that PSEG Long Island obtains and/or retains ownership of all rights to existing and future emission credits, renewable energy rights to existing and future emissions credits, renewable energy green tags, tradable renewable certificates and/or any and all other environmental benefits associated with the installation of the ECMs. Customer certifies that the information provided in the herein is true and accurate. Customer further certifies that the energy saving products described herein have or will be installed in the facility indicated above and will not be resold. As specified herein, Customer agrees to permit PSEG Long Island to: (1) verify the purchase invoices and product installations and (2) upon request, install and remove load-monitoring equipment at the facility. Customer acknowledges that the rights and obligations in this application shall be binding upon assignees, successors and future owners of the facility. Customer agrees to include restrictions contained in this agreement in any leases, sales, contracts, or other similar documents relating to the use and ownership of the facility. Customer acknowledge that, consistent with PSEG Long Island’s Efficiency Long Island program policies and procedures, PSEG Long Island may pro-rate a rebate or incentive (the “Rebate”) if the Customer purchases less than its full electric requirements from PSEG Long Island. Customer further acknowledges that PSEG Long Island may require the Customer to repay all or a portion of the Rebate received if, within five (5) years of receipt of the Rebate, the Customer ceases purchasing its full electric requirements from PSEG Long Island or increases its use of electric power from non-PSEG Long Island sources at the facility, other than through the Long Island Choice Program.
Customer Name: (Print)
Customer Signature: Duly authorized representative | [5 empty] | Date:
Project ID:
Application Version: | 4.1.2024_3 | [5 empty] | Effective: | 4.1.2024
Group Box 1260
Group Box 1286
Group Box 34
Group Box 34
Group Box 34

## Terms and Conditions
2024 Commercial Efficiency Program
Terms and Conditions
1. Rebates
a) | Subject to these Terms and Conditions, PSEG Long Island and/or its subsidiary, the Long Island Lighting Company d/b/a PSEG Long Island (hereinafter referred to individually or collectively as “PSEG Long Island”), will pay rebates to eligible Customers (hereinafter “Customers”) for the installation of Energy Conservation Measures (“ECMs”) listed on PSEG Long Island’s Commercial Efficiency Program (CEP)application forms.
b) | ECMs are those electric conservation measures identified as such in program materials issued by PSEG Long Island and other site-specific Custom or Whole Building Design Measures that are approved by PSEG Long Island. The installation of ECMs and other site-specific Custom or Whole Building Design Measures will be referred to as (“Project”) in these Terms and Conditions.
c) | All ECMs must be new equipment and installed by licensed contractors where required by code and/or law.
2. Customer Eligibility
a) | The PSEG Long Island Commercial Efficiency Program (“Program”) is available to all non-residential electric customers in the PSEG Long Island “Service Area,” which includes Nassau and Suffolk counties and a portion of Queens County known as the Rockaways.
b) | By participating in this Program, Customer agrees that PSEG Long Island obtains and/or retains ownership of all rights to existing and future emissions credits, renewable energy rights to existing and future emissions credits, renewable energy green tags, tradable renewable certificates and/or any and all other environmental benefits associated with the installation of the eligible equipment.
3. Pre-Approval and Pre-Installation Survey
a) | PSEG Long Island will not pay any rebates unless PSEG Long Island pre-approves the ECMs proposed by the Customer and completes, to PSEG Long Island’s satisfaction, a pre-installation survey of the Customer’s facilities, unless PSEG Long Island has expressly waived such pre-approval/inspection requirement.
b) | PSEG Long Island reserves sole discretion to approve or disapprove of any proposed ECMs.
4. Post-Installation Verification
PSEG Long Island will not pay any rebates until it has performed, to PSEG Long Island’s satisfaction a post-installation verification of the installation, unless PSEG Long Island has expressly waived such post-installation verification requirement. If PSEG Long Island determines that the ECMs were not installed in a manner that is consistent with the purpose of achieving energy savings, or if the installation was not consistent with generally accepted good engineering practices, PSEG Long Island reserves the right to require changes before making any rebate payments. PSEG Long Island will not pay rebates until it has been verified that the Customer has received, as appropriate, final drawings, operation and maintenance manuals, and operator training.
5. Customer Application and Analysis
a) | In addition to completing the application, the Customer may be required by PSEG Long Island to provide an analysis of the demand and energy reduction potential of the proposed ECMs. In some cases, a Professional Engineer licensed in the state of New York must prepare the analysis. Nameplate data may be required at PSEG Long Island’s discretion.
b) | PSEG Long Island may review the Customer’s application and analysis to make an independent determination of the energy saving and demand reduction potential. PSEG Long Island reserves the right to reject or modify any calculations, based on PSEG Long Island’s own analysis.
6. Site-Specific Custom Measures
PSEG Long Island will only approve of those site-specific Custom ECMs that PSEG Long Island believes have cost-effective energy and/or demand reduction potential. In any case, PSEG Long Island reserves sole discretion to approve or disapprove of payment of rebates for any such proposed ECMs.
7. Rebate Amounts
a) | Before pre-approving any rebate amounts requested by the Customer, PSEG Long Island reserves the right to adjust the rebate amount.
b) | Once a rebate amount is pre-approved, PSEG Long Island will pay the customer no more than 70% of the installed cost of the ECM, or the pre-approved rebate amount, whichever is less.
c) | PSEG Long Island reserves the right to lower the rebate amount if the quantity and/or cost of ECMs actually installed by the Customer differ from the pre-approved amounts.
d) | Notwithstanding any other provision of these Terms and Conditions, PSEG Long Island reserves the right to a refund of any rebates paid if, at any time, it learns that any agreed to ECMs were not actually, or properly installed, or have subsequently been disconnected.
e) | Custom Applications – The approved rebate cannot exceed PSEG Long Island’s electric savings benefits, as determined by PSEG Long Island through its analysis of the project
f) | PSEG Long Island reserves the right to withhold payment or to award the rebate in the form of a bill credit. Customers in arrears at the time of rebate payment may not be eligible to receive a rebate.
g) | The UL classification of Energy Verification Services (EVS) for the appropriate product classification is required. PSEG Long Island reserves the right to withhold rebate payments for or disqualify any ECM’s that do not carry the Underwriter’s Laboratory (UL) Classification Mark or, with the written consent of PSEG Long Island, an equivalent independent efficiency and product safety certification organization.
8. ECM and Installation Proof of Payment
a) | The Customer must provide copies of all invoices (including itemization of all materials, labor, and equipment discounts) reflecting the costs of purchasing and installing the ECMs. The invoices shall include a breakdown of all ECMs purchased for installation under the Program. In addition, PSEG Long Island may require any other reasonable documentation or verification of the cost to the Customer of purchasing and installing the ECM. PSEG Long Island may require invoices from Customer’s contractor to determine the price paid by the contractor (including any discounts or rebates) for the ECMs. For custom ECMs, PSEG Long Island reserves the right to use the contractor’s reasonable costs in order to determine the correct rebate amount.
b) | PSEG Long Island may require copies of the construction specifications, including relevant ECMs, provided to the construction/installation contractors for certain Projects. PSEG Long Island may refuse to pay rebates if the specifications do not adequately provide for installation of the ECMs consistent with good engineering and energy-efficient design practices. Customer will, upon request by PSEG Long Island, provide a copy of the as-built drawings and equipment submittals for the facility.
c) | Title to all of the equipment purchased under this agreement shall rest with the Customer.
9. Installation Service Costs Recognized
PSEG Long Island will recognize installation costs only to the extent that they are determined by PSEG Long Island to be reasonable and actually incurred by the Customer.
10. Contractor Shared Savings Arrangements
If Custom ECMs are being installed by Customer’s contractor under a “shared savings” contract or other situation where the customer’s contract is not based upon the price of installed equipment, PSEG Long Island reserves the right to determine the cost of purchasing and installing the ECMs based on the reasonable retail costs in purchasing the equipment and installing the ECMs.
11. Date of Rebate Payments
PSEG Long Island expects to pay the rebate within sixty (60) days after all of the following conditions are met: (1) construction/renovation of Customer’s facility is completed; (2) Customer has received an occupancy permit; and (3) PSEG Long Island has verified equipment and installation costs and satisfactory installation of the ECMs, all in accordance with the specifications. (4) All documents required by the application have been received by PSEG Long Island.
12. Replacement of Burn-Outs
Customers who install energy-efficient lighting ECMs are expected to replace any of the energy-efficient lights that burn out with lights of similar or superior energy savings efficiency at the Customer’s expense.
13. Monitoring and Evaluation Follow-up Visits
a) | PSEG Long Island reserves the right to make a reasonable number of installation follow-up visits to Customer’s Facility during the 24 months following the actual completion date noted on this application. Such visit(s) are not meant to inconvenience the Customer, PSEG Long Island, and the Customer agrees to provide access within a reasonable timeframe of receiving the request for a follow up visit.
b) | The purpose of the follow-up visit(s) is to provide PSEG Long Island with an opportunity to review the operation of the ECMs for program evaluation purposes.
14. Limited Scope of Review
PSEG Long Island is under no obligation to: (1) make follow-up visits, (2) review the operation of the ECMs, or (3) make any suggestions of any kind to the Customer.
The scope of review by PSEG Long Island of the design and installation of the ECMs is limited solely to determining whether Program conditions have been met. It does not include any kind of safety review.
15. Changes in the Program
a) | PSEG Long Island may change the program and the Terms & Conditions at any time without notice. PSEG Long Island, however, will process pre-approved applications, to completion under the Terms & Conditions in effect at the time of the pre-approval.
b) | PSEG Long Island reserves the right, for any reason, to stop pre-approving ECMs at any time without notice. In particular, PSEG Long Island is not obligated to pre-approve any application for an rebate that may result in PSEG Long Island exceeding its program budget
c) | The Program described in the application may be altered, suspended, or canceled by PSEG Long Island at any time without prior notice. Under such circumstances, the Customer is not entitled to any Program benefits in excess of those approved prior to such action by PSEG Long Island. Submission of a completed application does not entitle the Customer to program participation. Entitlement to Program participation can only occur after PSEG Long Island has signed a copy of the application and granted pre-approval
16. Payments Assignable to Contractors
The Customer may direct that rebates be paid directly to the Customer’s contractor. This request must be made expressly in writing.
17. Publicity of Customer Participation
PSEG Long Island may publicize the Customer’s participation in the Program, the results, the amount of rebates paid to the Customer, and any other information which reasonably relates to the Customer’s participation.
18. Installation Schedule Requirements
Where there is no deadline indicating otherwise on the application, PSEG Long Island may terminate the application and any approved rebate if the Customer is not engaged in installation of the pre-approved ECMs by the end of 180 days from the date PSEG Long Island approves the Customer’s Retrofit application and One year for all Custom applications.
19. Limitation of Liability and Indemnification
PSEG Long Island’s liability is limited to paying the approved rebates. . Neither PSEG Long Island, nor its affiliates, subsidiaries, Manager, employees, consultants, agents and contractors (“PSEG Long Island Parties”) shall be liable to the Customer for any consequential or incidental damages or for any damages in tort (including negligence) caused by any activities associated with this application or the Program.
The Customer shall protect, indemnify, and hold harmless PSEG Long Island, and the PSEG Long Island Parties from and against all liabilities, losses, claims, damages, judgments, penalties, causes of action, costs and expenses (including, without limitation, attorney’s fees and expenses) imposed upon or incurred by or assessed against PSEG Long Island, and the PSEG Long Island Parties resulting from, arising out of, or relating to the Program.
20. No Warranties
a) | PSEG Long Island does not endorse, guarantee, or warrant any particular manufacturer or product, and PSEG Long Island provides no warranties, expressed or implied, for any product or services.
b) | The Customer acknowledges that neither PSEG Long Island nor any of the PSEG Long Island Parties are responsible for assuring that the design, engineering and construction of Customer’s Project or that the installation of the ECMs is proper or complies with any particular laws (including patent laws), codes, or industry standards. PSEG Long Island does not make any representations of any kind regarding the results to be achieved by the ECMs or the adequacy or safety of such measures.
21. Customer Must Pay All Taxes
The benefits conferred upon the Customer through participation in this program may be taxable by the federal, state, and local government. The Customer is responsible for declaring any benefits and paying any associated taxes.
22. Pre-Approval Letter
After an application is approved by PSEG Long Island’s authorized executive, the Customer will receive written notification of the pre-approved rebate amount and the date that the ECMs must be fully installed to qualify for rebate payments. Any ECMs installed prior to the issuance of PSEG Long Island’s written authorization will be deemed as an unauthorized installation and PSEG Long Island will have no obligation to pay rebates for those ECMs.
23. Vendor Selection
It is the Customer’s responsibility to select a vendor to perform the work indicated on the Customer’s Application.
24. Removal of Equipment
The Customer agrees, as a condition of participation in the Program, to remove and dispose of all equipment being replaced by the ECMs and further agrees to carry out such removal and disposal in accordance with all laws, rules, and regulations. The Customer agrees not to reinstall any of this equipment in the Service Area of PSEG Long Island.
25. Miscellaneous
a) | By providing a telephone number you are giving consent to be contacted at that number about matters that are closely related to the utility service.
b) | These Terms and Conditions and program requirements outline the conditions under which PSEG Long Island will pay rebates. These Terms and Conditions are subject to change at PSEG Long Island’s discretion.
c) | If any provision of the Terms and Conditions is deemed invalid by any court or administrative body having jurisdiction, such ruling shall not invalidate any other provision, and the remaining Terms and Conditions shall remain in full force and effect in accordance with their terms.
d) | The Customer’s acceptance of final payment releases PSEG Long Island from all claims and liabilities to the Customer, and its representatives or assigns.
| I have read and understand the terms and conditions detailed above. |  | (initials)
| Application Version: | 4.1.2024_3 |  | Effective: | 4.1.2024

## Guidelines
2024 Commercial Efficiency Program
Guidelines
Rebate Guidelines
* | Do not use this application for Lighting and Standard rebates. For Lighting and Standard rebates please visit:
https://www.psegliny.com/businessandcontractorservices/businessandcommercialsavings/businessandcommercialrebates
* | For Multi Family projects, please refer to the Multi-Family application found on the PSEG Long Island website.
* | For Whole Building Heat Pump projects, refer to the Custom application found on the PSEG Long Island website.
- Heat Pump Rebates in application are available for Partial Building Heat Pumps only. Refer to "Part Building ccASHP Worksheet" tab.
* | Pre-approval is required.
* | Pre-inspection is required for all buildings. If there is no existing building (vacant lot) pre-inspection will not be required.
* | Project must be started after 4/1/2024 and completed within 180 days for existing buildings and 365 days for new construction, where there is a vacant lot at time of application submittal.
* | All projects are subject to Post-inspection.
* | If the proposed equipment is listed in the eligibility table, use the appropirate Worksheet to calculate the estimated rebate.
* | If the proposed equipment is not listed in the eligibility table, refer to the Custom/Custom Retrofit Eligibility requirements and documentation and contact a PSEG Long Island Representative or PSEG Long Island's Infoline at 1-800-692-2626. Rebate eligibility and amount will be calculated on a case by case basis.
* | Eligible equipment may be updated or modified regularly. For the most recent applications and worksheets please visit:
https://www.psegliny.com/businessandcontractorservices/businessandcommercialsavings/businessandcommercialrebates
* | Only applications and worksheets in effect at the time of submittal will be accepted. Please visit our website for the most recent applications and worksheets:
https://www.psegliny.com/businessandcontractorservices/businessandcommercialsavings/businessandcommercialrebates
* | Where eligible products are required to be listed with an approved rating agency (i.e. ENERGY STAR, CEE, NEEP, or other approved equivalent), products must be installed and used in accordance with the rating condition for which it was approved at the time such approval was given.
* | All measures must carry the appropriate designated Underwriters Laboratory (UL) or Electrical Testing Laboratory (ETL) label.
* | All installations must be installed in accordance with all applicable local, state and national codes and ordinances.
* | All eligibility requirements and deadlines apply. See the Eligibility Table tab for a comprehensive list of these requirements.
* | Total rebates will be capped at 70% of total project cost.
* | If submitting electronically, applicant must either submit an e-mail in lieu of signature or provide a hard copy with signature (fax, pdf, printed original, etc.).
* | If customer has participated in any other state or utility sponsored rebate program, related to the technology in this application, please contact a PSEG Long Island Representative to determine whether the project is also eligible under this program.
Program Requirements/Steps to Participate
* | Before you purchase and install equipment, send the following to PSEG Long Island to receive your Pre-Approval Letter:
* | Completed Customer Information section of application and appropriate worksheets. (Incomplete applications will not be accepted.)
* | Submit required documents (see Required Documents check sheet)
For Electronic Submissions e-mail documents to:
|  |  | CEPLI@pseg.com | or via Lead Partner Portal Online Application
Each required document must be a separate file (no zipped files)
Applications must be saved as: 24HVACWor_<<<customer Name>>MMDDYYYY.xls
For hardcopy submissions: PSEG Long Island CEP, 395 North Service Rd, Suite 409, Melville, NY 11747
* | AFTER you receive your Pre-Approval Letter, complete the project.
* | Once Project is Complete:
* | Submit copies of customer validated proof of payment (e.g. itemized invoice) showing the facility address, date and place of purchase and the model/part numbers of installed equipment.
* | A PSEG Long Island representative will contact you to schedule a post-inspection.
* | After verification that all necessary requirements have been met, a PSEG Long Island representative will authorize payment and either mail a check to the applicant/assignee or apply a bill credit to the applicant’s account.
| I have read and understand the Guidelines listed above. |  |  |  | (initials)
| Application Version: | 4.1.2024_3 |  |  |  | Effective: | 4.1.2024

## Required Documents
2024 Commercial Efficiency Program
Required Documents Check Sheet
Required Documents for All Projects
Document: |  | Responsible Party |  |  | Deliverable Timeline
|  | Customer |  |  | Pre-Installation
|  | Customer/Applicant |  |  | Pre-Installation
|  | Customer |  |  | Pre-Installation
|  | Customer/Applicant |  |  | Pre-Installation
|  | PSEG Long Island Project Manager |  |  | Pre-Installation
|  | Customer |  |  | Pre-Installation
|  | PSEG Long Island Project Manager |  |  | Pre-Installation
|  | Customer |  |  | Post-Installation
|  | Customer |  |  | Post-Installation
|  | PSEG Long Island Project Manager |  |  | Post-Installation
Required Documents for Part Building ccASHP Projects
Document: |  | Responsible Party |  |  | Deliverable Timeline
|  | Contractor |  |  | Pre-Installation
|  | Contractor |  |  | Pre-Installation
|  | Contractor |  |  | Pre-Installation
PSEG Long Island may require additional documentation not listed in the check boxes above as deemed necessary to properly process any rebates.
I have read and understand the information listed above. |  |  | (initials)
Application Version: | 4.1.2024_3 |  |  | Effective: | 4.1.2024
Completed Worksheet
New Equipment
Replacement Equipment
Assignment Letter (only required if rebate is assigned to contractor)
Cut Sheets for All Measures (must identify model number)
Proof of Payment (reflecting total installed cost)
W9 Form
Certification of Completion
Pre-Inspection
Completed Worksheet
Vendor's Proposal (including itemized labor and materials)
Signed Application
Post-Inspection
Manual N Load Calculations
AHRI Certificate
NEEP Certificate (for all ccASHP projects)

## Eligibility Table
Commercial Efficiency Program
Air Conditioning and Heat Pump Eligibility Tables
If the proposed equipment either does not meet the eligibility requirements or is not listed below, the applicant may still be eligible for a Custom Rebate. Contact a PSEG Long Island representative or the PSEG Long Island infoline at 1-800-692-2626.
Eligibility Requirements
n | Projects must be completed within 180 days of pre approval for all retrofit applications and one year for new construction.
n | New equipment must be of the same size as existing equipment in order to be eligible for rebates offered in this workbook; for all other replacement types please contact your PSEG Long Island representative.
n | Rebates are performance based, and calculated from a baseline of ASHRAE 90.1 2016 unless existing efficiencies are provided
- All Partial Building Cold Climate Air Source Heat Pumps are paid on a $/Ton Basis and available on the "Part Building ccASHP Worksheet" tab.
n | Projects installing Whole Building heat pumps must go through the custom program and use the NYS Clean Heat Calculator found on the PSEG Long Island website.
n | Variable Refrigerant Flow (VRF) heat pump installations must go through the custom program and use the NYS Clean Heat Calculator found on the PSEG Long Island website.
| Air Conditioning |  |  |  | For new equipment or replacement of existing equipment
| Equipment Type | Sample Photo | Size Category | Sub Category | New Equipment Efficiency | Code | Rebate $/kWh
| Packaged Terminal Air Conditioners (PTAC) |  | < 0.75 Tons | All Types | 12.2 EER | PTAC101 | 0.55
|  |  | > 0.75 Tons & < 1 Ton | All Types | 11.4 EER | PTAC201 | 0.55
|  |  | > 1 Ton | All Types | 10.4 EER | PTAC301 | 0.55
| Ductless Mini-Split AC |  | < 5.4 Tons | All Types | 15.0 SEER 12.5 EER | AC201 | 0.55
| Air conditioners, Air cooled (Cooling Mode) |  | < 5.4 Tons | Split System | 16.0 SEER 13.0 EER | AC311 | 0.55
|  |  |  | Single Package | 16.0 SEER 12.0 EER | AC321 | 0.55
|  |  | ≥ 5.4 & < 11.25 Tons | Split System | 12.6 EER 17 IEER | AC411 | 0.55
|  |  |  | Single Package | 12.6 EER 17 IEER | AC421 | 0.55
|  |  | ≥ 11.25 & < 20 Tons | Split System | 12.3 EER 16.5 IEER | AC511 | 0.55
|  |  |  | Single Package | 12.3 EER 16.5 IEER | AC521 | 0.55
|  |  | ≥ 20 & < 63 Tons | Split System | 11.5 EER 16 IEER | AC611 | 0.55
|  |  |  | Single Package | 11.5 EER 16 IEER | AC621 | 0.55
| Air Conditioners, Water and Evaporatively Cooled |  | All Sizes | Split System | 14.0 EER | AC811 | 0.55
|  |  |  | Single Package | 14.0 EER | AC821 | 0.55
HVAC equipment efficiency criteria are based on applicable AHRI standards at AHRI standard conditions using a non-CFC refrigerant.
| Packaged Terminal Heat Pumps |  |  |  | For new equipment or replacement of existing equipment
| Equipment Type | Sample Photos | Size Category | Sub Category | New Equipment Efficiency | Code | Rebate $/ton
| Packaged Terminal Heat Pumps (PTHPs) |  | < 0.75 tons | All Types | 12.2 EER 3.5 COP | PTHP101 | 600
|  |  | > 0.75 tons & < 1 ton | All Types | 11.4 EER 3.3 COP | PTHP201
|  |  | > 1 ton | All Types | 10.4 EER 3.1 COP | PTHP301
| Ductless Mini-Split Heat Pumps |  | < 5.4 Tons | All Types | 15.0 SEER 12.5 EER 8.5 HSPF | HP101 | 2
| Air Cooled Heat Pumps |  | < 5.4 Tons | Split System | 15.0 SEER 12.5 EER 8.5 HSPF | HP211 | 2
|  |  |  | Single Package | 15.0 SEER 12.0 EER 8.2 HSPF | HP221 | 2
|  |  | ≥ 5.4 & < 11.25 tons | Split System | 14.5 IEER 12.1 EER 3.5 COP | HP311 | 2
|  |  |  | Single Package | 14.5 IEER 12.1 EER 3.5 COP | HP321 | 2
|  |  | ≥ 11.25 & < 20 Tons | Split System | 13.9 IEER 12.4 EER 3.4 COP | HP411 | 2
|  |  |  | Single Package | 13.9 IEER 12.4 EER 3.4 COP | HP421 | 2
|  |  | ≥ 20 & < 63 Tons | Split System | 12.9 IEER 11.8 EER 3.3 COP | HP511 | 2
|  |  |  | Single Package | 12.9 IEER 11.8 EER 3.3 COP | HP521 | 2
| Ductless Mini-Split Cold Climate Heat Pump |  | All Sizes | N/A | 18.0 SEER 10.0 HSPF | CCHP101 | 2
| Ducted Cold Climate Heat Pump |  | All Sizes | N/A | 17.0 SEER 10.0 HSPF | CCHP211 | 2
| Water Source Heat Pumps |  | < 11.25 Tons | N/A | 14.0 EER 4.6 COP | HP601 | 2
All Whole Building Heat Pumps must go Custom.
HVAC equipment efficiency criteria are based on applicable AHRI standards at AHRI standard conditions using a non-CFC refrigerant.
| Variable Refrigerant Flow Multisplit Heat Pumps |  |  |  | For new equipment or replacement of existing equipment
| Equipment Type | Sample Phots | Size Category | Sub Category | New Equipment Efficiency | Code | Rebate $/kWh
| VRF Air Cooled |  | < 5.4 Tons | Multisplit System | 15.0 SEER 12.5 EER 8.5 HSPF | VHP211 | 0.55
|  |  | ≥ 5.4 & < 11.25 Tons | Multisplit System | 14.6 IEER 11.3 EER 3.4 COP | VHP311 | 0.55
|  |  | ≥ 11.25 & < 20 Tons | Multisplit System | 13.9 IEER 10.9 EER 3.2 COP | VHP321
|  |  | ≥ 20 Tons | Multisplit System | 12.7 IEER 10.3 EER 3.2 COP | VHP411 | 0.55
| VRF Water Source |  | < 11.25 Tons | Multisplit System | 14.0 EER 4.6 COP | VHP421
| VRF Water Source (Heating Mode) |  | < 11.25 Tons | 68° Entering Water | 4.6 COP |  | 80
Note: Rebates for VRFs are only available for replacement of existing Multisplit systems
Note: VRFs installed in place of all other scenarios may be eligibile for a Custom Rebate
| Partial Building Cold Climate Air Source Heat Pump |  |  |  | For new equipment
| Equipment Type | Description | Size Category | Replacement Type | New Equipment Efficiency | Code | Rebate $/ton | Bonus Rebate $/ton* | Bonus DAC Rebate $/ton**
| Ductless Mini-Split Cold Climate Heat Pump | -Ductless Mini-Split is a Single Zone application -AHRI Capacity at 17⁰F must meet at least 65-135% of the calculated heating load -Must be installed with Integrated Modulating Controls if fossil fuel heaters are still present | All Sizes | New Construction | Must be NEEP Listed | CCHP101-NC | 600 | 750 | 900
|  |  |  | Fossil Fuel Replacement |  | CCHP101-OC
|  |  |  | All Others |  | CCHP101-AO
| Ductless Multi-Split Cold Climate Heat Pump | -Ductless Multi-Split is a Multiple Zone application -AHRI Capacity at 17⁰F degrees must meet at least 65-135% of the calculated heating load -Must be installed with Integrated Modulating Controls if fossil fuel heaters are still present | All Sizes | New Construction | Must be NEEP Listed | CCHP151-NC | 600 | 750 | 900
|  |  |  | Fossil Fuel Replacement |  | CCHP151-OC
|  |  |  | All Others |  | CCHP151-AO
| Ducted Cold Climate Heat Pump | -Centrally Ducted System -AHRI Capacity at 17⁰F degrees must meet at least 65-135% of the calculated heating load | All Sizes | New Construction | Must be NEEP Listed | CCHP211-NC | 600 | 750 | 900
|  |  |  | Fossil Fuel Replacement |  | CCHP211-OC
|  |  |  | All Others |  | CCHP211-AO
| Integrated/Modulating Control | -The ASHP and backup heating system are on the same thermostat -The backup heater can modulate to meet the load without limiting the ASHP from delivering its maximum capacity -Also called “perfect” control | N/A | N/A | N/A | CEP405 | $500/project
| Integrated/Fixed Control | -The ASHP and backup heating system are on the same thermostat -The backup heater has a fixed capacity to meet the load -The backup heater is larger than the ASHP, so the ASHP is not always able to deliver its maximum capacity (the backup heater supplies a larger share of the load when both are running) | N/A | N/A | N/A | CEP406 | $500/project
| Dual Fuel Thermostat | -The central ASHP is installed on the same ductwork as the fuel-fired furnace -Once the ASHP can no longer meet the load (or when a changeover temperature is reached) -The ASHP shuts off and the furnace meets the load | N/A | N/A | N/A | CEP410 | $500/project
*In order to qualify for the per Ton rebates in the above listed table, all projects must be started after April 1, 2024 and completed within 180 days of pre-approval
**Disadvantaged Community (DAC) rebates are available to customers who are located within a Disadvantaged Community; refer to the Disadvantaged Community dropdown on the Customer Information tab PSEG Long Island will make the final determination if a customer is located within a Disadvantaged Community
Rebates are based on 17°F Rated Heating Capacity
Note: In order for a heat pump to qualify as cold climate, it must appear on the NEEP cold climate list. Please note, all Whole Building projects must go Custom. The above rebates are for Part Building Heat Pumps only.
Note: Fossil Fuel Replacement = Oil No Central Air Conditioner, All Others = All Other Scenarios
| Ventilation Equipment |  |  |  | For new equipment or replacement of existing equipment
| Equipment Type | Description | Size Category | Replacement Type | New Equipment Efficiency | Code | Rebate
| Energy Recovery Ventilator (ERV) | Transfers both sensible (heat content) and latent (moisture content) heat between supply and exhaust airstreams. | All Sizes | Existing Building | N/A | V100 | $70/100CFM
| Heat Recovery Ventilator (HRV) | Transfers sensible heat only between supply and exhaust airstreams | All Sizes | Existing Building | N/A | V110 | $60/100CFM
| High Volume Low Speed Fans (HVLS) | HVLS fans are ceiling mounted fans that move large amounts of air more efficiently and with lower noise levels | >=16 feet diameter | All Building Type | N/A | V200 | $50/ Ft. Diameter
ERV/HRV installation only eligible for retrofit purpose only. New installation will not be eligible for the rebate. Please use Ventilation tab to enter the equipment details and to determine the eligible rebate
| Application Version: | 4.1.2024_3 |  |  |  | Effective Date: | 4.1.2024

## HVAC Worksheet
Commercial Efficiency Program
HVAC Rebate Worksheet, Version 3
| Effective Date : | 4.1.2024 | [20 empty] | Project Summary
| Account Name : |  |  | Building Type : | Select … | [17 empty] | Total kW Savings:
| Facility Address : |  |  | Account # : | [18 empty] | Total kWh Savings:
| City, State, Zip : |  |  | Phone : | [18 empty] | Total MMBTU Savings:
| Contact Name / Title : |  |  | Fax : | [18 empty] | Total Calculated Rebate :
| E-mail : |  |  | Cell : | [18 empty] | Total Estimated Rebate: | 0 | #VALUE!
Project ID:
[16 empty] | *Please note that ASHRAE 90.1 2016 will be used as the baseline if existing information is unavailable | [6 empty] | *Please enter a Building Type*
| New Unit | [10 empty] | Installed Cost |  |  | Existing Unit
| Equipment Type | Size Category | Sub Category | Manufacturer | Model Number | Size (tons) | Quantity | SEER/IEER | EER | HSPF | COP | Material Per Unit | Labor Per Unit | Total Per Unit | Cooling Equipment (required) | Primary Heating Fuel Type (required) | Model Number (if available*) | SEER/IEER/IPLV (if available*) | EER (if available*) | HSPF (if available*) | COP (if available*) | Heater AFUE | Equipment Status | Total Rebate
Ex. | Air Conditioners - Air Cooled | < 5.4 Tons | Split System | Trane | YHC024 | 5 | 3 | 16 | 13 | 8.5 | 3.5 | 5000 | 1500 | 6500 | Room Air Conditioner | Gas |  | 13 | 9 | 8.5 | 1 | 80%
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
| Application Version: | 4.1.2024_3 | [20 empty] | Effective: | 4.1.2024
Group Box 649

## Part Building ccASHP Worksheet
Commercial Efficiency Program
Partial Building Heat Pump Worksheet, Version 3
| Effective Date : | 4.1.2024 |  | 4.1.2024
1. To be eligible for the rebates on this worksheet, a cold climate air source heat pump (ccASHP) must be installed.
2. The ccASHP must be sized at 17⁰F to meet at least 65%-135% of the building's total heating load.
3. Eligible ccASHP equipment must be found on the NEEP Cold Climate ASHP list.
| 4. Contractors must supply a Manual N, or Load Calculations showing the total cooling and heating load for the building. | [25 empty] | Project Summary
| 5. The ccASHP installed must be variable capacity. | [28 empty] | FAIL
| 6. If the customer is keeping the existing fossil fuel system, or is installing a new fossil fuel system, integrated controls or a dual fuel thermostat must also be installed. | [25 empty] | Total kW Savings: | 0
| -See NYSERDA's list of Qualified Integrated Controls for more information: |  |  |  | https:\\nyserda.ny.gov/qualified-integrated-controls | [21 empty] | Total kWh Savings: | 0
| Integrated Controls | [25 empty] | Total MMBTU Savings: | 0 |  | #VALUE!
| Control Type |  |  | Manufacturer | Approved Thermostat |  |  | Model Number |  | Customer Rebate |  |  |  |  | Building Type : | Select … | [10 empty] | Total Calculated Rebate :
| Dual Fuel Thermostat |  |  | Ecobee | Ecobee 4 |  |  | EB-STATE4*** | [18 empty] | Total Estimated Rebate:
0
*Please Enter Integrated Controls Information Above*
| New Unit | [11 empty] | Manual N |  |  | Installed Cost |  |  | Existing Unit
| Equipment Type | Size Category | Sub Category | Manufacturer | Model Number | AHRI Reference ID | 95°F Rated Cooling Capacity (Btuh) (From NEEP List) | 17°F Rated Heating Capacity (Btuh) (From NEEP List) | SEER/IEER | EER | HSPF | COP | Cooling Load | Heating Load |  | Material Per Unit | Labor Per Unit | Total Per Unit | Cooling Equipment (required) | Primary Heating Fuel Type (required) | Model Number (if available) | SEER/IEER/IPLV (if available) | EER (if available) | HSPF (if available) | COP (if available) | Heater AFUE | Equipment Status | Total Customer Rebate | Total Contractor Incentive
Ex. | Cold Climate Air Source Heat Pumps | < 5.4 Tons | Split System | Trane | YHC024 | 5593485 | 36000 | 36000 | 18 | 13 | 10 |  | 34000 | 36000 |  | 5000 | 1500 | 6500 | Room Air Conditioner | Oil |  | 13 | 10 | 8 | 1 | 80%
1 | [5 empty] | 5593485
2 | [5 empty] | 5593486
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
| Application Version: | 4.1.2024_3 |  | 4.1.2024_3 | [22 empty] | Effective: | 4.1.2024
Note on C18: Rush, Meaghan C (US): Remove auto "All Size"
Group Box 649

## Ventilation
Commercial Efficiency Program
Ventilation, Version 3
Project Summary
| Effective Date : | 4.1.2024
Total kW Savings:
| Account Name : |  |  | Building Type : | Select … | [11 empty] | Total kWh Savings:
| Facility Address : |  |  | Account # : | [12 empty] | Total MMBTU Savings:
| City, State, Zip : |  |  | Phone : | [12 empty] | Total Calculated Rebate :
| Contact Name / Title : |  |  | Fax : | [12 empty] | Total Estimated Rebate: | 0
| E-mail : |  |  | Cell : | [17 empty] | #VALUE!
Project ID:
Energy Recovery Ventilator & Heat Recovery Ventilator (ERV / HRV)
*Please note that ASHRAE 90.1 2016 will be used as the baseline if existing information is unavailable
| New Unit | [6 empty] | Installed Cost |  |  | Existing Unit | [7 empty] | Result
| Equipment Type | ERV/HRV Equipment CFM | Sensible HX Efficiency | Total HX Efficiency | Delta P (Inch of Water) | Facility Operating Hours Profile |  | Material Per Unit | Labor Per Unit | Total Cost | Equipment Type (Required) | Primary Heating Fuel Type (Required) | Size Category (Required) | Model Number (If Available) | SEER / IEER (If available) | HSPF (Only for Electric Heating) | Boiler / Furnace AFUE (If available) |  | Rebate
Ex | Heat Recovery Ventilator (HRV) | 1000 | 70% | 55% | 1 | Mon - Fri 7AM-5PM |  | 500 | 500 | 1000 | Air Conditioners - Air Cooled | Oil | ≥ 11.25 & < 20 Tons | 456 | 11 |  | 80% |  | 600
1 | [18 empty] | 0
2 | [18 empty] | 0
3 | [18 empty] | 0
4 | [18 empty] | 0
5 | [18 empty] | 0
6 | [18 empty] | 0
7 | [18 empty] | 0
8 | [18 empty] | 0
9 | [18 empty] | 0
10 | [18 empty] | 0
High Volume Low Speed Fans (HVLS)
| New Unit | [6 empty] | Installed Cost |  |  | Existing Unit |  |  |  |  | Result
| Fan Type | Building Construction Type | lbf/Fan | Fan lbf/kW | Units | Operating Hours | VFD Control | Material Per Unit | Labor Per Unit | Total Cost | Fan Type (Required) | lbf/Fan | Fan lbf/kW | Units |  | Rebate
Ex | 24 Feet HVLS | Existing Building | 20000 | 200 | 5 | 5000 | Yes | 2500 | 1000 | 17500 | 48" - 52" Diameter | 20000 | 15 | 5 |  | 6000
1
2
3
4
5
6
7
8
9
10
| Application Version: | 4.1.2024_3 | [17 empty] | Effective: | 4.1.2024
Group Box 649

## Inspection Form (hidden)
2024 Commercial Efficiency Program
HVAC Inspection Form 2024 version - 3
|  | Workbook Name : | PSEGLI_2023 HVAC Worksheet_VERSION 1.0.xlsm
Project ID :
|  | Account Name : |  |  |  | Confirmation
Facility Address :
|  | City, State, Zip: |  |  |  |  | Inspector Name: |  |  | Signature :
Contact Name / Title :
|  | Phone : |  |  |  |  | Inspector Company Name: |  |  | Date:
Cell :
|  | Building Type: | Select … |  |  |  | Customer Name: |  |  | Customer Signature:
Additional Projects to Inspect:
1. Have you or any family member traveled to a country for which the CDC has issued a Lvel 2 or 3 travel designation within the last 14 days?
2. Have you or a family member traveled or had contact with any Persons Under Investigation (PUIs) for COVID-19 within the last 14 days, OR with anyone with known COVID-19?
3. Do you or any family member have any symptoms of a fever or respiratory infection (e.g., cough, sore throat, fever, or shortness of breath)?
IF ANY QUESTION IS RESPONDED TO WITH A YES, YOU CANNOT PROCEED AND WILL NEED TO RESCHEDULE THE APPOINTMENT
Project ID :
Pre Inspection
| Unit ID | Equipment Type |  | Existig Heating Fuel | Qty. | Manufacturer | Model No. | Serial No. | Verified | Images | Comments
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Post Inspection
| Unit ID | Equipment Type |  | Unit Size | Qty. | Manufacturer | Model No. | Serial No. | Verified | Images | Comments
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Yes
Yes
Yes
No
No
No

## ccASHP Inspection Form (hidden)
2024 Commercial Efficiency Program
HVAC Inspection Form 2024 version - 3
|  | Workbook Name : | PSEGLI_2023 HVAC Worksheet_VERSION 1.0.xlsm
Project ID :
|  | Account Name : |  |  |  | Confirmation
Facility Address :
|  | City, State, Zip: |  |  |  |  | Inspector Name: |  |  | Signature :
Contact Name / Title :
|  | Phone : |  |  |  |  | Inspector Company Name: |  |  | Date:
Cell :
|  | Building Type: | Select … |  |  |  | Customer Name: |  |  | Customer Signature:
Additional Projects to Inspect :
1. Have you or any family member traveled to a country for which the CDC has issued a Lvel 2 or 3 travel designation within the last 14 days?
2. Have you or a family member traveled or had contact with any Persons Under Investigation (PUIs) for COVID-19 within the last 14 days, OR with anyone with known COVID-19?
3. Do you or any family member have any symptoms of a fever or respiratory infection (e.g., cough, sore throat, fever, or shortness of breath)?
IF ANY QUESTION IS RESPONDED TO WITH A YES, YOU CANNOT PROCEED AND WILL NEED TO RESCHEDULE THE APPOINTMENT
Project ID :
Pre Inspection
| Unit ID | Equipment Type |  | Existig Heating Fuel | Qty. | Manufacturer | Model No. | Serial No. | Verified | Images | Comments
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Post Inspection
| Unit ID | Equipment Type |  | Unit Size (Cooling Btu) | Unit Size (Heating Btu) | Manufacturer | Model No. | Serial No. | Verified | Images | Comments
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Yes
Yes
Yes
No
No
No

## ERV-HRV Inspection Form (hidden)
2024 Commercial Efficiency Program
ERV-HRV Inspection Form 2024 version - 3
|  | Workbook Name : | PSEGLI_2023 HVAC Worksheet_VERSION 1.0.xlsm
Project ID :
|  | Account Name : |  |  |  | Confirmation
Facility Address :
|  | City, State, Zip: |  |  |  |  | Inspector Name: |  |  | Signature :
Contact Name / Title :
|  | Phone : |  |  |  |  | Inspector Company Name: |  |  | Date:
Cell :
|  | Building Type: | Select … |  |  |  | Customer Name: |  |  | Customer Signature:
Additional Projects to Inspect:
1. Have you or any family member traveled to a country for which the CDC has issued a Lvel 2 or 3 travel designation within the last 14 days?
2. Have you or a family member traveled or had contact with any Persons Under Investigation (PUIs) for COVID-19 within the last 14 days, OR with anyone with known COVID-19?
3. Do you or any family member have any symptoms of a fever or respiratory infection (e.g., cough, sore throat, fever, or shortness of breath)?
IF ANY QUESTION IS RESPONDED TO WITH A YES, YOU CANNOT PROCEED AND WILL NEED TO RESCHEDULE THE APPOINTMENT
Project ID :
Pre Inspection
| Unit ID | Equipment Type |  | Existig Heating Fuel | Qty. | Equipment Size | Model No. | Size Category | Verified | Images | Comments
1
2
3
4
5
6
7
8
9
10
Post Inspection
| Unit ID | Equipment Type |  | Unit Size CFM | Qty. | Model No |  | Facility Operating Hour Profile | Verified | Images | Comments
1
2
3
4
5
6
7
8
9
10
Yes
Yes
Yes
No
No
No

## HVLS Inspection Form (hidden)
2024 Commercial Efficiency Program
HVLS Inspection Form 2024 version - 3
|  | Workbook Name : | PSEGLI_2023 HVAC Worksheet_VERSION 1.0.xlsm
Project ID :
|  | Account Name : |  |  |  | Confirmation
Facility Address :
|  | City, State, Zip: |  |  |  |  | Inspector Name: |  | Signature :
Contact Name / Title :
|  | Phone : |  |  |  |  | Inspector Company Name: |  | Date:
Cell :
|  | Building Type: | Select … |  |  |  | Customer Name: |  | Customer Signature:
Additional Projects to Inspect:
1. Have you or any family member traveled to a country for which the CDC has issued a Lvel 2 or 3 travel designation within the last 14 days?
2. Have you or a family member traveled or had contact with any Persons Under Investigation (PUIs) for COVID-19 within the last 14 days, OR with anyone with known COVID-19?
3. Do you or any family member have any symptoms of a fever or respiratory infection (e.g., cough, sore throat, fever, or shortness of breath)?
IF ANY QUESTION IS RESPONDED TO WITH A YES, YOU CANNOT PROCEED AND WILL NEED TO RESCHEDULE THE APPOINTMENT
Project ID :
Pre Inspection
| Unit ID | Existing Fan Size |  | Operating Hours | Qty. | Verified | Images | Comments
1
2
3
4
5
6
7
8
9
10
Post Inspection
| Unit ID | Equipment Type |  | Operating Hours | Qty. | Verified | Images | Comments
1
2
3
4
5
6
7
8
9
10
Yes
Yes
Yes
No
No
No

## Summary
Account Name :
Project ID:
Measure Code | Quantity | Gross kW Savings per Unit | Gross kWh Savings per Unit | Gross MMBtu Savings per Unit | Total kW Savings | Total EE kWh Savings | Total MMBtu Savings | Total Rebate
AC100
AC200
AC201
AC202
AC310
AC311
AC312
AC320
AC321
AC322
AC410
AC411
AC412
AC420
AC421
AC422
AC510
AC511
AC512
AC520
AC521
AC522
AC610
AC611
AC612
AC620
AC621
AC622
AC710
AC711
AC712
AC720
AC721
AC722
AC811
AC821
PTAC101
PTAC201
PTAC301
GHP100
GHP101
GHP102
GHP200
GHP201
GHP202
GHP300
GHP301
GHP302
VHP211
VHP212
VHP311
VHP321
VHP411
VHP421
HP100
HP101
HP102
HP211
HP212
HP221
HP222
HP311
HP321
HP411
HP421
HP511
HP521
HP601
PTHP101
PTHP201
PTHP301
CCHP101
CCHP101-NC
CCHP101-OC
CCHP101-AO
CCHP151
CCHP151-NC
CCHP151-OC
CCHP151-AO
CCHP211
CCHP211-NC
CCHP211-OC
CCHP211-AO
CEP405
CEP406
CEP410
V100
V110
V200
HVAC Worksheet Totals | [7 empty] | 0
WB ccASHP Totals | [7 empty] | 0
Ventilation Worksheet Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Utility Gross kW | $/kW | Total MMBTU Savings | Total Calculated Rebate
[5 empty] | 0 |  | 0 | 0

## Calculations (hidden)
#N/A
Customer Inputs | [6 empty] | 2 | [43 empty] | Tier 1 & Tier 2 |  | 0.3 | [5 empty] | #VALUE! |  | #REF!
|  |  |  | Existing Equipment Type | Existing Criteria |  |  |  | New Unit |  |  |  | Minimum Requirement |  |  |  |  | PASS/FAIL | [5 empty] | Building | [7 empty] | Existing/Baseline Equipment |  | Existing/Baseline Unit | [5 empty] | Parasitics | Cooling | Cooling | Cooling Savings | Cooling Savings | Fossil Fuel Heating Savings | Heating | Heating | Fossil Fuel Heating Savings | Heating Savings | Added Heating | Electric Heating Savings | FF + E Heating Savings | Total Combined | Cooling | Heating | Combined | Cooling | Heating | Combined | EEkWh | EE kWh | [7 empty] | EE CO2 Savings | BE CO2 Savings | Utility Gross kW
| New Equipment Type | Size Category | Sub Category |  |  | VLOOKUP | Tons | Quantity | SEER | EER | HSPF | COP | SEER | EER | HSPF | COP | RAC Only | SEER | EER | HSPF | COP | RAC only | Final | Type | FLCH | FLHH |  |  |  |  | VLOOKUP | Cooling Equipment | Heating equipment | SEER | EER | HSPF | COP | AFUE | Displacement | (kWh/MMBTU) | kW per Unit | Total kW | kWh per Unit | MMBTU per Unit | MMBtu per Unit | kW per Unit | Total kW | kWh Parasitics | kWh per Unit | kWh per Unit | MMBtu per Unit | MMBtu per Unit | kWh per Unit | Total kWh | Total kWh | Total kWh | Total MMBtu | Total MMBtu | Total MMBtu | per unit | Total | Rebate | Total Rebate ($) |  | VLOOKUP | Tier | VLOOKUP | Code | Total Savings (lbs) | Total Savings (lbs) | Total Savings
Ex. | [29 empty] | Ex. | [33 empty] | Ex.
1 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 1 |  |  | #N/A | [5 empty] | #N/A | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 1 |  |  |  |  | #VALUE! | #VALUE! | 0
2 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 2 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 2 |  |  |  |  | #VALUE! | #VALUE! | 0
3 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 3 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 3 |  |  |  |  | #VALUE! | #VALUE! | 0
4 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 4 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 4 |  |  |  |  | #VALUE! | #VALUE! | 0
5 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 5 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 5 |  |  |  |  | #VALUE! | #VALUE! | 0
6 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 6 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 6 |  |  |  |  | #VALUE! | #VALUE! | 0
7 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 7 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 7 |  |  |  |  | #VALUE! | #VALUE! | 0
8 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 8 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 8 |  |  |  |  | #VALUE! | #VALUE! | 0
9 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 9 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 9 |  |  |  |  | #VALUE! | #VALUE! | 0
10 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 10 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 10 |  |  |  |  | #VALUE! | #VALUE! | 0
11 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 11 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 11 |  |  |  |  | #VALUE! | #VALUE! | 0
12 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 12 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 12 |  |  |  |  | #VALUE! | #VALUE! | 0
13 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 13 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 13 |  |  |  |  | #VALUE! | #VALUE! | 0
14 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 14 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 14 |  |  |  |  | #VALUE! | #VALUE! | 0
15 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 15 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 15 |  |  |  |  | #VALUE! | #VALUE! | 0
16 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 16 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 16 |  |  |  |  | #VALUE! | #VALUE! | 0
17 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 17 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 17 |  |  |  |  | #VALUE! | #VALUE! | 0
18 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 18 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 18 |  |  |  |  | #VALUE! | #VALUE! | 0
19 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 19 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 19 |  |  |  |  | #VALUE! | #VALUE! | 0
20 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 20 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 20 |  |  |  |  | #VALUE! | #VALUE! | 0
21 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 21 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 21 |  |  |  |  | #VALUE! | #VALUE! | 0
22 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 22 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 22 |  |  |  |  | #VALUE! | #VALUE! | 0
23 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 23 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 23 |  |  |  |  | #VALUE! | #VALUE! | 0
24 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 24 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 24 |  |  |  |  | #VALUE! | #VALUE! | 0
25 | [22 empty] | FAIL | Select … | #N/A | #N/A |  |  |  | 25 | [8 empty] | 1 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 25 |  |  |  |  | #VALUE! | #VALUE! | 0
Small Buiness Heating
|  |  |  | Existing Equipment Type | Existing Heating Type |  |  | Cooling | Heating | New Unit |  |  |  | Minimum Requirement |  |  |  | PASS/FAIL |  |  |  | Building |  |  | Manual N check | [7 empty] | Existing/Baseline Equipment |  | Existing/Baseline Unit | [5 empty] | WB | WB | WB | WB | WB | WB | WB | WB | EER | COP | COP | Cooling | Heating | Cooling Savings | Cooling Savings | Fossil Fuel Heating Savings | Heating Savings | Added Heating | Electric Heating Savings | FF + E Heating Savings | Total Combined | Cooling | Heating | Combined | Cooling | Heating | Combined | EE kWh |  |  | Contractor |  |  | EE CO2 Savings | BE CO2 Savings | Utility Gross kW
| New Equipment Type | Size Category | Sub Category |  |  | Scanario | VLOOKUP | Btu | Btu | SEER | EER | HSPF | COP | SEER | EER | HSPF | COP | SEER | EER | HSPF | COP | Type | FLCH | FLHH | Cooling Load | Heating Load | Heating Min | Heating Max | PASS/FAIL | Final |  | VLOOKUP | Cooling Equipment | Heating equipment | SEER | EER | HSPF | COP | AFUE | HPSizing Ratio | Scenario | a | b | c | d | F cooling | F heating | F HSPF | Seasonal,ee | Seasonal,ee | Seasonal,baseline | kW per Unit | kW per Unit | kWh per Unit | MMBTU per Unit | MMBtu per Unit | kWh per Unit | kWh per Unit | MMBtu per Unit | MMBtu per Unit | kWh per Unit | Total kWh | Total kWh | Total kWh | Total MMBtu | Total MMBtu | Total MMBtu | Total | Rebate | Total Rebate ($) | Incentive | VLOOKUP | Code | Total Savings | Total Savings | Total Savings
Ex. | [30 empty] | Ex.
1 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 1 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
2 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 2 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
3 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 3 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
4 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 4 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
5 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 5 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
6 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 6 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
7 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 7 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
8 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 8 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
9 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 9 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
10 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 10 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
11 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 11 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
12 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 12 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
13 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 13 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
14 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 14 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
15 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 15 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
16 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 16 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
17 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 17 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
18 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 18 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
19 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 19 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
20 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 20 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
21 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 21 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
22 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 22 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
23 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 23 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
24 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 24 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
25 | [5 empty] | All Other | [15 empty] | Select … | #N/A | #N/A | [5 empty] | FAIL | 25 | [8 empty] | 0.5 | [28 empty] | 0 | #VALUE! | 0 | All Other |  |  |  | 0
Ventilation
|  |  |  | Total HX Efficiency | Delta P (Inch of Water) | Facility Operating Hour Profile | Existing Unit | [5 empty] | Vlookup | ASHRAE 90.1 2016 Values if Existing value not present |  |  | Building | [5 empty] | ERV Energy Savings | [11 empty] | HRV Energy Savings | [11 empty] | Rebate |  | Rebate Cap at Cost
| New Equipment Type | ERV/HRV CFM | Sensible HX Efficiency |  |  |  | Equipment Type | Primary Heating Fuel Type | Size Category | SEER / IEER | HSPF | Boiler/Furnace AFUE |  | SEER/IEER | HSPF | Boiler/Furnace AFUE | Type | FLCH | FLHH |  |  |  | Fan kW | Boiler Furnace AFUE | HSPF | SEER/IEER | Cooling kWh | Cooling MMBTU | Heating kWh | Heating MMBTU | Total Electric Savings kWh | Total Peak Demand Savings kW | Total MMBTU Savings | Utility Gross kW | Fan kW | Boiler Furnace AFUE | HSPF | SEER/IEER | Cooling kWh | Cooling MMBTU | Heating kWh | Heating MMBTU | Total Electric Savings kWh | Total Peak Demand Savings kW | Total MMBTU Savings | Utility Gross kW | ERV Rebate | HRV Rebate | ERV Rebate | HRV Rebate
Ex | Heat Recovery Ventilator (HRV) | 1000 | 0.7 | 0.55 | 1 | Mon - Fri 7AM-5PM | Air Conditioners - Air Cooled | Oil | ≥ 11.25 & < 20 Tons | 11 |  | 0.8 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons |  |  |  | Mon - Fri 7AM-5PM | 890 | 1663 |  |  |  |  | 0.8 |  | 11 | #VALUE! | #VALUE! |  | 26.4018 | 0 | 0 | 0 |  | 0.25064 | 0.8 |  | 11 | 2.6371 | 0.0089979 |  | 26.4018 | 2.6371 | 0.0023705 | 26.4108 |  | 700 | 600
1 | [17 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE! | #VALUE! |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
2 | [17 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE! | #VALUE! |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
3 | [17 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE! | #VALUE! |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
4 | [17 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE! | #VALUE! |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
5 | [17 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE! | #VALUE! |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
6 | [17 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE! | #VALUE! |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
7 | [17 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE! | #VALUE! |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
8 | [17 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE! | #VALUE! |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
9 | [17 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE! | #VALUE! |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
10 | [17 empty] | 0 | 0 | [7 empty] | #VALUE! | #VALUE! |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE! | #VALUE! |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
HVLS
| New Unit | [5 empty] | Existing Unit | [5 empty] | Energy Savings Calcs | [6 empty] | Rebate
| Fan Type | Building Construction Type | lbf/Fan | Fan lbf/kW | Units | VFD Control | Operating hours | Fan Type (Required) | lbf/Fan | Fan lbf/kW | Units |  | Existing Units | Existing lbf/kW | lbf/Fan | Electric Savings kWh | Peak kW Savings | Total MMBTU Savings | Utility Gross kW Savings | Feet | $
Ex | 24 Feet HVLS | Existing Building | 20000 | 200 | 5 | 0.75 | 5000 | 48" - 52" Diameter | 20000 | 15 | 5 |  | 5 | 15 | 20000 | 30833.3333 | 4.9452 | 105.2033 |  | 24 | 6000
1 | [5 empty] | 1 | 4988 |  |  | 16 |  |  | 5 | 16 |  | #VALUE! |  | 0 | 0 | #N/A
2 | [5 empty] | 1 | 4988 |  |  | 16 |  |  | 5 | 16 |  | 0 | 0 | 0 | 0 | #N/A
3 | [5 empty] | 1 | 4988 |  |  | 16 |  |  | 5 | 16 |  | 0 | 0 | 0 | 0 | #N/A
4 | [5 empty] | 1 | 4988 |  |  | 16 |  |  | 5 | 16 |  | 0 | 0 | 0 | 0 | #N/A
5 | [5 empty] | 1 | 4988 |  |  | 16 |  |  | 5 | 16 |  | 0 | 0 | 0 | 0 | #N/A
6 | [5 empty] | 1 | 4988 |  |  | 16 |  |  | 5 | 16 |  | 0 | 0 | 0 | 0 | #N/A
7 | [5 empty] | 1 | 4988 |  |  | 16 |  |  | 5 | 16 |  | 0 | 0 | 0 | 0 | #N/A
8 | [5 empty] | 1 | 4988 |  |  | 16 |  |  | 5 | 16 |  | 0 | 0 | 0 | 0 | #N/A
9 | [5 empty] | 1 | 4988 |  |  | 16 |  |  | 5 | 16 |  | 0 | 0 | 0 | 0 | #N/A
10 | [5 empty] | 1 | 4988 |  |  | 16 |  |  | 5 | 16 |  | 0 | 0 | 0 | 0 | #N/A

## ProposedEquipment0 (hidden)
Row Number | BaseLine Row_ID | Product Line | Product Class | Product Name | Product Quantity | Application ID | Location | Operating Hours | Measure Code | Baseline SEER | Baseline EER | Baseline HSPF | Baseline COP | Proposed/Installed SEER | Proposed/Installed EER | Proposed/Installed HSPF | Proposed/Installed COP | Coincidence Factor | Free Ridership | Spillover | full load heating hours | full load cooling hours | Gross Savings Per Unit - kWh | Gross Savings Per Unit - kW | In Service Rate | Utility Gross kW | Utility Gross kWh | Net Per Unit kWh | Net Per Unit kW | Per Unit CO2 Savings | Per Unit MMBTU Savings | Equipment Cost | Labor Cost | Total Cost | Manufacturer | Model | Tons | Elec Util Cust Incentive | Incentive Per Unit | Workbook Name
1 | [31 empty] | 0 | 0 | [6 empty] | PSEGLI_2023 HVAC Worksheet_VERSION 1.0_draft6.xlsm
2 | [31 empty] | 0 | 0 | [6 empty] | PSEGLI_2023 HVAC Worksheet_VERSION 1.0_draft6.xlsm
3 | [31 empty] | 0 | 0 | [6 empty] | PSEGLI_2023 HVAC Worksheet_VERSION 1.0_draft6.xlsm
4 | [31 empty] | 0 | 0
5 | [31 empty] | 0 | 0
6 | [31 empty] | 0 | 0
7 | [31 empty] | 0 | 0
8 | [31 empty] | 0 | 0
9 | [31 empty] | 0 | 0
10 | [31 empty] | 0 | 0
11 | [31 empty] | 0 | 0
12 | [31 empty] | 0 | 0
13 | [31 empty] | 0 | 0
14 | [31 empty] | 0 | 0
15 | [31 empty] | 0 | 0
16 | [31 empty] | 0 | 0
17 | [31 empty] | 0 | 0
18 | [31 empty] | 0 | 0
19 | [31 empty] | 0 | 0
20 | [31 empty] | 0 | 0
21 | [31 empty] | 0 | 0
22 | [31 empty] | 0 | 0
23 | [31 empty] | 0 | 0
24 | [31 empty] | 0 | 0
25 | [31 empty] | 0 | 0

## HVAC Types (hidden)
| Product Line | Product Class | Product Name
AC100 | Cooling - HVAC Equipment | Air Conditioners | ACR Room Air Conditioners - AC100
AC200 | Cooling - HVAC Equipment | Air Conditioners | ACR Ductless Mini Split - AC200
AC201 | Cooling - HVAC Equipment | Air Conditioners | ACR Ductless Mini-Split AC - AC201
AC202 | Cooling - HVAC Equipment | Air Conditioners | ACR Ductless Mini-Split AC - AC202
AC300 | Cooling - HVAC Equipment | Air Conditioners | ACR Small Commercial Split - AC300
AC310 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC310
AC311 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC311
AC312 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC312
AC320 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC320
AC321 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC321
AC322 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC322
AC400 | Cooling - HVAC Equipment | Air Conditioners | ACR Packaged Air Conditioner - AC400
AC410 | Cooling - HVAC Equipment | Air Conditioners | ACR Packaged Air Conditioner - AC410
AC411 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC411
AC412 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC412
AC420 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC420
AC421 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC421
AC422 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC422
AC510 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC510
AC511 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC511
AC512 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC512
AC520 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC520
AC521 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC521
AC522 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC522
AC610 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC610
AC611 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC611
AC612 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC612
AC620 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC620
AC621 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC621
AC622 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC622
AC710 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC710
AC711 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC711
AC712 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC712
AC720 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC720
AC721 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC721
AC722 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC722
AC811 | Cooling - HVAC Equipment | Air Conditioners | ACR Evaporatively Cooled AC Split - AC811
AC821 | Cooling - HVAC Equipment | Air Conditioners | ACR Evaporatively Cooled AC Packaged - AC821
PTAC101 | Cooling - HVAC Equipment | Air Conditioners | ACR Packaged Termincal AC - PTAC101
PTAC201 | Cooling - HVAC Equipment | Air Conditioners | ACR Packaged Termincal AC - PTAC201
PTAC301 | Cooling - HVAC Equipment | Air Conditioners | ACR Packaged Termincal AC - PTAC301
GHP100 | Cooling - HVAC Equipment | Heat Pump | ACR Geothermal Heat Pump Closed Loop - GHP100
GHP101 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Closed Loop - GHP101
GHP102 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Closed Loop - GHP102
GHP200 | Cooling - HVAC Equipment | Heat Pump | ACR Geothermal Heat Pump Open Loop - GHP200
GHP201 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Open Loop - GHP201
GHP202 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Open Loop - GHP202
GHP300 | Cooling - HVAC Equipment | Heat Pump | ACR Geothermal Heat Pump Direct Geoexchange - GHP300
GHP301 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Direct Geoexchange - GHP301
GHP302 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Direct Geoexchange - GHP302 | VRF Air Cooled | < 5.4 Tons | Multisplit System
HP100 | Cooling - HVAC Equipment | Heat Pump | ACR Ductless Mini-Split Heat Pump - HP100
HP101 | Cooling - HVAC Equipment | Heat Pump | ACR Ductless Mini-Split Heat Pump - HP101 |  | ≥ 5.4 & < 11.25 Tons | Multisplit System
HP102 | Cooling - HVAC Equipment | Heat Pump | ACR Ductless Mini-Split Heat Pump - HP102 |  | ≥ 11.25 & < 20 Tons | Multisplit System
HP211 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Split - HP211 |  | ≥ 20 Tons | Multisplit System
HP212 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Split - HP212 | VRF Water Source | < 11.25 Tons | Multisplit System
HP221 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Packaged - HP221
HP222 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Packaged - HP222
HP311 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Split - HP311
HP321 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Packaged - HP321
HP411 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Split - HP411
HP421 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Packaged - HP421
HP511 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Split - HP511
HP521 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Packaged - HP521
HP601 | Cooling - HVAC Equipment | Heat Pump | ACR Water Source Heat Pump - HP601
PTHP101 | Cooling - HVAC Equipment | Heat Pump | ACR Packaged Terminal Heat Pump - PTHP101
PTHP201 | Cooling - HVAC Equipment | Heat Pump | ACR Packaged Terminal Heat Pump - PTHP201
PTHP301 | Cooling - HVAC Equipment | Heat Pump | ACR Packaged Terminal Heat Pump - PTHP301
VHP211 | Cooling - HVAC Equipment | Heat Pump | VRF Water Source Heat Pump - VHP211
VHP212 | Cooling - HVAC Equipment | Heat Pump | VRF Air Cooled Heat Pump - VHP212
VHP311 | Cooling - HVAC Equipment | Heat Pump | VRF Air Cooled Heat Pump - VHP311
VHP321 | Cooling - HVAC Equipment | Heat Pump | VRF Air Cooled Heat Pump - VHP321
VHP411 | Cooling - HVAC Equipment | Heat Pump | VRF Air Cooled Heat Pump - VHP411
VHP421 | Cooling - HVAC Equipment | Heat Pump | VRF Air Cooled Heat Pump - VHP421
CCHP101 | Cooling - HVAC Equipment | Heat Pump | Ductless Mini-Split Cold Climate Heat Pump - CCHP101
CCHP101-NC | Cooling - HVAC Equipment | Heat Pump | Ductless Mini-Split Cold Climate Heat Pump - CCHP101-NC
CCHP101-OC | Cooling - HVAC Equipment | Heat Pump | Ductless Mini-Split Cold Climate Heat Pump - CCHP101-OC
CCHP101-AO | Cooling - HVAC Equipment | Heat Pump | Ductless Mini-Split Cold Climate Heat Pump - CCHP101-AO
CCHP151 | Cooling - HVAC Equipment | Heat Pump | Ductless Multi-Split Cold Climate Heat Pump - CCHP151
CCHP151-NC | Cooling - HVAC Equipment | Heat Pump | Ductless Multi-Split Cold Climate Heat Pump - CCHP151-NC
CCHP151-OC | Cooling - HVAC Equipment | Heat Pump | Ductless Multi-Split Cold Climate Heat Pump - CCHP151-OC
CCHP151-AO | Cooling - HVAC Equipment | Heat Pump | Ductless Multi-Split Cold Climate Heat Pump - CCHP151-AO
CCHP211 | Cooling - HVAC Equipment | Heat Pump | Ducted Cold Climate Heat Pump - CCHP211
CCHP211-NC | Cooling - HVAC Equipment | Heat Pump | Ducted Cold Climate Heat Pump - CCHP211-NC
CCHP211-OC | Cooling - HVAC Equipment | Heat Pump | Ducted Cold Climate Heat Pump - CCHP211-OC
CCHP211-AO | Cooling - HVAC Equipment | Heat Pump | Ducted Cold Climate Heat Pump - CCHP211-AO
CEP405 | Cooling - HVAC Equipment | Cooling & Controls | Cooling HVAC Equipment - CEP405
CEP406 | Cooling - HVAC Equipment | Cooling & Controls | Cooling HVAC Equipment - CEP406
CEP410 | Cooling - HVAC Equipment | Cooling & Controls | Cooling HVAC Equipment - CEP410
CEP402 | Cooling - HVAC Equipment | Cooling & Controls | Cooling HVAC Equipment - CEP402
| Cooling - HVAC Equipment | Air Conditioners | Evaporatively Cooled Unitary Air Conditioner - <65,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Evaporatively Cooled Unitary Air Conditioner - >=135,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Evaporatively Cooled Unitary Air Conditioner - >=65,000 Btuh and <135,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Split A/C <65,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Split A/C >=135,000 Btuh and <240,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Split A/C >=240,000 Btuh and <760,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Split A/C >=65,000 Btuh and <135,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Split A/C >=760,000 Btuh and <3,600,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Unitary A/C <65,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Unitary A/C >=135,000 Btuh and <240,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Unitary A/C >=240,000 Btuh and <760,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Unitary A/C >=65,000 Btuh and <135,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Unitary A/C >=760,000 Btuh and <3,600,000 Btuh
| Cooling - HVAC Equipment | Air Conditioners | Whole Building - HVAC
| Cooling - HVAC Equipment | Heat Pump | Heat Pump - Split or Packaged - >= 65,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Packaged Heat Pump <65,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Split Heat Pump <65,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Split Heat Pump >=135,000 Btuh and <240,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Split Heat Pump >=240,000 Btuh and <760,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Split Heat Pump >=65,000 Btuh and <135,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Split Heat Pump >=760,000 Btuh and <3,600,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Unitary Heat Pump <65,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Unitary Heat Pump >=135,000 Btuh and <240,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Unitary Heat Pump >=240,000 Btuh and <760,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Unitary Heat Pump >=65,000 Btuh and <135,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Unitary Heat Pump >=760,000 Btuh and <3,600,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Water Source Heat Pump (Cooling Only)
| Cooling - HVAC Equipment | Heat Pump | Water Source Heat Pump (Cooling Only) <17,000 Btuh
| Cooling - HVAC Equipment | Heat Pump | Water Source Heat Pump (Cooling Only) >=17,000
| Code | Equipment
| AC100 | Room Air Conditioners < 2.5 Tons All Types Tier 0
| AC200 | Ductless Mini-Split AC < 5.4 Tons All Types Tier 0
| AC201 | Ductless Mini-Split AC < 5.4 Tons All Types Tier 1
| AC202 | Ductless Mini-Split AC < 5.4 Tons All Types Tier 2
| AC310 | Air Conditioners - Air Cooled < 5.4 Tons Split System Tier 0
| AC311 | Air Conditioners - Air Cooled < 5.4 Tons Split System Tier 1
| AC312 | Air Conditioners - Air Cooled < 5.4 Tons Split System Tier 2
| AC320 | Air Conditioners - Air Cooled < 5.4 Tons Single Package Tier 0
| AC321 | Air Conditioners - Air Cooled < 5.4 Tons Single Package Tier 1
| AC322 | Air Conditioners - Air Cooled < 5.4 Tons Single Package Tier 2
| AC410 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System Tier 0
| AC411 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System Tier 1
| AC412 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System Tier 2
| AC420 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package Tier 0
| AC421 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package Tier 1
| AC422 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package Tier 2
| AC510 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System Tier 0
| AC511 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System Tier 1
| AC512 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System Tier 2
| AC520 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package Tier 0
| AC521 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package Tier 1
| AC522 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package Tier 2
| AC610 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System Tier 0
| AC611 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System Tier 1
| AC612 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System Tier 2
| AC620 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package Tier 0
| AC621 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package Tier 1
| AC622 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package Tier 2
| AC710 | Air Conditioners - Air Cooled ≥ 63 Tons Split System Tier 0
| AC711 | Air Conditioners - Air Cooled ≥ 63 Tons Split System Tier 1
| AC712 | Air Conditioners - Air Cooled ≥ 63 Tons Split System Tier 2
| AC720 | Air Conditioners - Air Cooled ≥ 63 Tons Single Package Tier 0
| AC721 | Air Conditioners - Air Cooled ≥ 63 Tons Single Package Tier 1
| AC722 | Air Conditioners - Air Cooled ≥ 63 Tons Single Package Tier 2
| AC811 | Air Conditioners - Water & Evaporatively Cooled All Sizes Split System Tier 1
| AC821 | Air Conditioners - Water & Evaporatively Cooled All Sizes Single Package Tier 1
| GHP100 | Geothermal Heat Pumps < 11.25 Tons Closed Loop Tier 0
| GHP101 | Geothermal Heat Pumps < 11.25 Tons Closed Loop Tier 1
| GHP102 | Geothermal Heat Pumps < 11.25 Tons Closed Loop Tier 2
| GHP200 | Geothermal Heat Pumps < 11.25 Tons Open Loop Tier 0
| GHP201 | Geothermal Heat Pumps < 11.25 Tons Open Loop Tier 1
| GHP202 | Geothermal Heat Pumps < 11.25 Tons Open Loop Tier 2
| GHP300 | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) Tier 0
| GHP301 | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) Tier 1
| GHP302 | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) Tier 2
| HP100 | Ductless Mini-Split Heat Pumps < 5.4 Tons All Types Tier 0
| HP101 | Ductless Mini-Split Heat Pumps < 5.4 Tons All Types Tier 1
| HP102 | Ductless Mini-Split Heat Pumps < 5.4 Tons All Types Tier 2
| HP211 | Air Cooled Heat Pumps < 5.4 Tons Split System Tier 1
| HP212 | Air Cooled Heat Pumps < 5.4 Tons Split System Tier 2
| HP221 | Air Cooled Heat Pumps < 5.4 Tons Single Package Tier 1
| HP222 | Air Cooled Heat Pumps < 5.4 Tons Single Package Tier 2
| HP311 | Air Cooled Heat Pumps ≥ 5.4 & < 11.25 tons Split System Tier 1
| HP321 | Air Cooled Heat Pumps ≥ 5.4 & < 11.25 tons Single Package Tier 1
| HP411 | Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Split System Tier 1
| HP421 | Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Single Package Tier 1
| HP511 | Air Cooled Heat Pumps ≥ 20 & < 63 Tons Split System Tier 1
| HP521 | Air Cooled Heat Pumps ≥ 20 & < 63 Tons Single Package Tier 1
| HP601 | Water Source Heat Pumps < 11.25 Tons N/A Tier 1

## Old Summary (hidden)
2012 Commercial Efficiency Program
Summary Table
| Air Conditioning |  |  |  | For replacement of Existing Equipment in working condition | [7 empty] | For new equipment or replacement of Existing Equipment that does not meet the conditions in the previous columns
[13 empty] | Tier 1 | [6 empty] | Tier 2
| Equipment Type | Size Category | Sub Category | VLOOKUP | Code | Quantity | Gross kW per Unit | Gross kWh per Unit | Total kW | Total kWh | Total Rebate | Code | Quantity | Gross kW per Unit | Gross kWh per Unit | Total kW | Total kWh | Total Rebate | Code | Quantity | Gross kW per Unit | Gross kWh per Unit | Total kW | Total kWh | Total Rebate
| Room Air Conditioners | < 2.5 Tons | All Types | Room Air Conditioners < 2.5 Tons All Types | AC101 |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
| Ductless Mini-Split AC | < 5.4 Tons | All Types | Ductless Mini-Split AC < 5.4 Tons All Types | AC201 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC202 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC203 |  | #REF! | #REF! | #REF! | #REF! | #REF!
| Air Conditioners - Air Cooled | < 5.4 Tons | Split System | Air Conditioners - Air Cooled < 5.4 Tons Split System | AC301 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC302 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC303 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | Single Package | Air Conditioners - Air Cooled < 5.4 Tons Single Package | AC401 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC402 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC403 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  | ≥ 5.4 & < 11.25 Tons | Split System | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System | AC501 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC502 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC503 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | Single Package | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package | AC601 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC602 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC603 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  | ≥ 11.25 & < 20 Tons | Split System | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System | AC701 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC702 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC703 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | Single Package | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package | AC801 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC802 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC803 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  | ≥ 20 & < 63 Tons | Split System | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System | AC901 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC902 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC903 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | Single Package | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package | AC800 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC1002 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC1003 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  | ≥ 63 Tons | Split System | Air Conditioners - Air Cooled ≥ 63 Tons Split System | AC900 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC1102 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC1103 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | Single Package | Air Conditioners - Air Cooled ≥ 63 Tons Single Package | AC1001 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC1202 |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC1203 |  | #REF! | #REF! | #REF! | #REF! | #REF!
| Air Conditioners - Water & Evaporatively Cooled | All Sizes | Split System | Air Conditioners - Water & Evaporatively Cooled All Sizes Split System |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC1100 |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | Single Package | Air Conditioners - Water & Evaporatively Cooled All Sizes Single Package |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | AC1200 |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
| Heat Pumps |  |  |  |  | For replacement of Existing Equipment in working condition | [6 empty] | For new equipment or replacement of Existing Equipment that does not meet the conditions in the previous columns
[13 empty] | Tier 1 | [6 empty] | Tier 2
| Equipment Type | Size Category | Sub Category | VLOOKUP | Code | Quantity | Gross kW per Unit | Gross kWh per Unit | Total kW | Total kWh | Total Rebate | Code | Quantity | Gross kW per Unit | Gross kWh per Unit | Total kW | Total kWh | Total Rebate | Code | Quantity | Gross kW per Unit | Gross kWh per Unit | Total kW | Total kWh | Total Rebate
| Ductless Mini-Split Heat Pump | < 5.4 Tons | All Types | Ductless Mini-Split Heat Pump < 5.4 Tons All Types | HP101 |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP102 |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP103 |  | #REF! | #REF! | #REF! | #REF! | #REF!
| Air Cooled Heat Pumps | < 5.4 Tons | Split System | Air Cooled Heat Pumps < 5.4 Tons Split System |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP201 |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP202 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | Single Package | Air Cooled Heat Pumps < 5.4 Tons Single Package |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP301 |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP302 |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  | ≥ 5.4 & <11.25 tons | Split System | Air Cooled Heat Pumps ≥ 5.4 & <11.25 tons Split System |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP401 |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | Single Package | Air Cooled Heat Pumps ≥ 5.4 & <11.25 tons Single Package |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP501 |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  | ≥ 11.25 & < 20 Tons | Split System | Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Split System |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP601 |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | Single Package | Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Single Package |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP701 |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  | ≥ 20 & < 63 Tons | Split System | Air Cooled Heat Pumps ≥ 20 & < 63 Tons Split System |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP801 |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  |  | Single Package | Air Cooled Heat Pumps ≥ 20 & < 63 Tons Single Package |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP901 |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
| Water Source Heat Pumps | < 11.25 Tons | N/A | Water Source Heat Pumps < 11.25 Tons N/A |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | HP1001 |  | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
| Application Totals |  |  |  |  | 0 |  |  | #REF! | #REF! | #REF! |  | 0 |  |  | #REF! | #REF! | #REF! |  | 0 |  |  | #REF! | #REF! | #REF!

## Development (hidden)
Commercial Efficiency Program
HVAC Worksheet
2024 | Program Year
3 | Current Version (Customer Inputs, Eligibility Table)
4.1.2024 | Current Effective Date (Eligibility Table)
date | description | initials | version
10.24.11 | Initial Draft Worksheet Developed | SN | R0.00
10.24.11 | Initial HVAC Worksheet Created (Modified from Previous Version) | SN | NC6.01
Re-arranged layout
Revised Calculations
Added Energy Savings Calculations
Updated cell references to Named ranges instead of Row/Column range references
11.15.11 | Update Worksheet to fix bugs, make similar to Lighting Retrofit Worksheet | SN | R0.01
Added Instructions, Eligibility Table and Development tab
11.21.11 | Added 15 EER, 30 SEER maximums to Customer Inputs tab | SN | R0.02
Changed Calculations in Eff-Size Qualification tab. Only returns Pass/Fail as a result now
Updated cell references to Named ranges instead of Row/Column range references
Added Building Type drop-down to Customer Inputs tab
11.21.11 | Edited Instruction Sheet | JR | R0.03
11.22.11 | Edited Instruction Sheet | SN | R0.04
Corrected Existing Equipment Type dropdown
Created Summary tab
Removed Heating inputs/calculations
11.22.11 | Released as Version 1.00 | SN | R1.00
12.06.11 | Updated Summary tab | SN | R1.01
12.06.11 | Added Instructions, Eligibility Table and Development tab | SN | NC6.02
Added Building Type drop-down to Customer Inputs tab
12.07.11 | Added Clear Inputs Button and Macro | SN | NC6.02
Added Zoom Macro
12.08.11 | Update Worksheet to fix bugs, make similar to AC Retrofit Worksheet | SN | NC6.02
Changed Calculations in Eff-Size Qualification tab. Only returns Pass/Fail as a result now
Edited Instruction Sheet
Fixed Name References
12.08.11 | Added 15 EER, 30 SEER maximums to Customer Inputs tab | SN | NC6.03
12.30.11 | Merged Existing and New HVAC Worksheets into Complete HVAC Worksheet | SN | 1.00
01.03.12 | Edited changes between two worksheets | SN | 1.03
01.05.12 | Updated Data Validation lists on Customer Inputs tab | SN | 1.04
01.06.12 | Updated WorksheetOpen() macro to work with Excel 2010 Protected View | SN | 1.06
Added Auto Zoom button
01.06.12 | Fixed differences in References causing errors in calculating rebate values | SN | 1.07
01.09.12 | Removed IF(Proposed EER ≤ 0,FAIL) in "New Unit Test - EER" in Eff-Size Qualification tab | SN | 1.08
01.09.12 | Added Summary tab | SN | 1.09
Required both categories (EER:EER, SEER:SEER, HSPF:HSPF, COP:COP) present for calculations
Changed Room AC requirements from 12.0 SEER to 10.4 EER
Restarted Numbering
01.12.12 | Split Summary into Tier 1 and Tier 2 | SN | 2012 - 1.00
01.30.12 | Expanded manufacturer's list | KM | 2012 - 1.0
1.31.12 | Removed required fields for Mfr and Model | JR | 2012 - 1.1
| Deleted the drop down list for Mfr | JR | 2012 - 1.1
3.28.12 | Created new summary table | KM | 2012 - 1.2
3.28.12 | Changed password | SN | 2012 - 1.2
Updated version
3.29.12 | Populated new summary table with lookups | SN | 2012 - 1.2
3.30.12 | Edited Instruction Sheet | SN | 2012 - 1.2
Added Lock/Unlock sheet Macro
Changed EER base for <5.4 Tons from 11.8 to 11.1
4.20.12 | Corrected qualification for AC Retrofit on air cooled AC < 5.4 tons single package | JR | 2012 - 1.2
5.14.12 | Updated Total Rebate on Summary Tab | SN | 2012 - 1.3
Updated Lookup table for HP311 and HP321
6.18.12 | Geothermal categories added to eligibility table | KM | 2012 - 1.4
6.25.12 | Updated sheet to include geothermal categories | SN | 2012 - 1.4
6.26.12 | Updated baseline for geothermal categories (used to calculate energy savings) | SN | 2012 - 1.4
Updated EER max entry value on Customer Inputs sheet to 35
Added Lock/Unlock buttons to Development Tab
7.10.12 | Updated Minimums for Geothermal DX Equipment | SN | 2012 - 1.4
7.11.12 | Updated Eligiblity Table & Minimums for All Geothermal Equipment | SN | 2012 - 1.4
7.19.12 | Added toggle switch between NC and Retrofit sheets | SN | 2012 - 1.4
7.23.12 | Updated toggle switch code | SN | 2012 - 1.4
7.25.12 | Updated title header | SN | 2012 - 1.4
7.27.12 | Fixed Tier 0 lookups for existing unit minimums | SN | 2012 - 1.4
7.31.12 | Updated Existing Equipment Dropdown List | SN | 2012 - 1.4
Updated T0 Reference Table
Added Existing Unit Dropdown Lookup Reference Table
Removed Existing Unit Dropdown Static Reference Table
8.27.12 | Added cost Field to Customer Inputs tab | KM | 2012 - 1.4
8.28.12 | Added Application ID to both Customer Inputs and Summary tabs | KM | 2012 - 1.4
8.28.12 | Added Customer Name to Summary tab | KM | 2012 - 1.4
Restarted Numbering for New Year
10.18.12 | Created HVAC Types tab and ProposedEquipment0 tab | KM | 2013 - 1.0
10.18.12 | Linked Version Number, Program Year and Program Name in headers to Development tab | KM | 2013 - 1.0
10.18.12 | Fixed Object Movement problem on front page | SN | 2013 - 1.0
10.18.12 | Updated HVAC Inventory name (affected Clear All Inputs) | SN | 2013 - 1.0
12.12.12 | Made Cost data required fields | KM | 2013 - 1.0
12.12.12 | Added note "Cost data required" to Customer inputs sheet | KM | 2013 - 1.0
4.24.13 | Increased all rebate levels; updated eligibility table and references tab | KM | 2.0
4.25.13 | Changed version number | KM | 2.0
4.25.13 | Added "Limited time only" banner to eligibility table | KM | 2.0
4.30.13 | Edits made to eligibility table, heading text will change in Tier I & II columns depending on NC or EB toggle | SN | 2.0
7.25.13 | Modified Summary results for specific TRC project, The Rinx project | KM | 2.1
7.25.13 | Correction made to summary tab, kW savings were being double counted when the same device was used on multiple lines. | KM | 2.2
7.25.13 | Version changed to 2.2 | KM | 2.2
7.25.13 | Changed Manufacturer and model number cells to gray for customer input | KM | 2.2
8.1.13 | Correction made to summary tab, kWh savings were being double counted when the same device was used on multiple lines. | KM | 2.2
8.1.13 | Edited the reference to manufacturer on the Proposed 0 which was previously pointing to model | KM | 2.2
8.16.13 | Changed version number and effective date to 3.0, 9/1/13 | KM | 3.0
9.24.13 | Changed version number to 1.0, year to 2014 and start date to 10.1.13 | KM | 1.0
9.24.13 | Removed all Not for Profit references | KM | 1.0
9.24.13 | Changed incentive amounts back to what they were prior to stimulus HVAC tab | KM | 1.0
9.24.13 | Removed reference to Stimulus | KM | 1.0
9.24.13 | Changed password to monkey | KM | 1.0
9.26.13 | Changed Version number to 4.0 and program year back to 2013 | KM | 4.0
9.26.13 | Added text "Projects must be completed by 3/31/14 to Eligibility Table
10.17.13 | Added field, "Elec Util Cust Incentive" to ProposeEquipment0 tab to import rebate amounts. | KM | 1.0
11.21.13 | Corrected error on Customer Inputs tab, formula in row 32, column x had been deleted. Formula has been added back in. | KM | 1.0
12.12.13 | Removed Color Change Macros for Existing vs. New Construction | SN | 1.0
12.12.13 | Changed PSEGLI logo to PSEG logo | SN | 1.0
12.12.13 | Cell Fill Effects, Cell Color Backgrounds, and Text Color changed on Instruction, Inputs, Summary, and Eligibility Table | SN | 1.0
12.13.13 | Added logic to limit rebates to a maximum of $2,500/kW | KM | 1.0
12.26.13 | Added rebate cap of 70% of installed cost | KM | 1.0
4.10.14 | Corrected Total Expected Rebate field on Customer Inputs tab. Calculation did not account for multiple units per line or multiple lines. | KM | 1.2
4.10.14 | Changed PSEGLI to PSEG Long Island throughout workbook | KM | 1.2
6.10.14 | Corrected LOOKUP on ProposedEquipment0 tab; reference table was not sorted properly resulting in incorrect Product Names, issue has been corrected | KM | 2.0
6.10.14 | Edited Conditional Formatting for Ductless Mini-Split Heat Pumps that are replaceing Room AC, SEER, HSPF and COP will now be grayed out on for Existing Equipment | KM | 2.0
6.10.14 | Changed version to 2.0 | KM | 2.0
10.10.14 | Changed version to 1.0 and program year to 2015 | IM | 1.0
3.25.15 | Increased rebate amount from $300 to $450 on AC310 & AC320 | KM | 2.0
3.25.15 | Increased rebate amount from $400 to $500 on AC410 & AC420 | KM | 2.0
11.25.15. | Corrected Summary tab to include new VRF measures | KM | 1.1
11.25.15 | Defined Named Range for all data to be imported into Captures | KM | 1.1
5.11.16 | Updated effective date to 6.15.16 and version number to 2.0 | KM | 2.0
5.11.16 | Added Inspection Form | KM | 2.0
6.17.16 | Increased Geothermal Incentive amounts | KM | 2.0
10.28.16 | Added Customer Information tab | KM | 1.0
10.28.16 | Updated Customer information tab with new effective date of 12.1.16 and version number | KM | 1.0
10.28.16 | Removed Application Type from Customer Info tab | KM | 1.0
10.28.16 | Added Project Type to Customer Info tab | KM | 1.0
10.28.16 | Added PTAC and PTHP units | KM | 1.0
10.28.16 | Updated all efficiency requirements and baselines | KM | 1.0
10.28.16 | Baselines are from ASHRAE 90.1 2013 | KM | 1.0
10.28.16 | Added SEER and IEER to the eligibilty table | KM | 1.0
10.28.16 | Made IEER or SEER required where applicable | KM | 1.0
10.28.16 | Added size cap of 63 tons | KM | 1.0
11.18.16 | Made references to Customer Information page to fill out Customer Inputs general information section and stopped the Clear Inputs button from clearing those contents. | MVG | 1.0
11.21.16 | Update baseline based on ASHRAE 90.1-2013 (Air Conditioner, Air Cooled <5.4 tons Single Package) | MVG | 1.0
11.21.16 | Update baseline based on ASHRAE 90.1-2013 (VRF Air Cooled Heat Pumps ≥ 5.4 & < 11.25 Tons Multisplit System) | MVG | 1.0
11.21.16 | Update baseline based on ASHRAE 90.1-2013 (VRF Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Multisplit System) | MVG | 1.0
11.21.16 | Update baseline based on ASHRAE 90.1-2013 (VRF Air Cooled Heat Pumps ≥ 20 Tons Multisplit System) | MVG | 1.0
11.21.16 | Update baseline based on ASHRAE 90.1-2013 (Geothermal Heat Pumps < 11.25 Tons Closed Loop) | MVG | 1.0
11.21.16 | Update baseline based on ASHRAE 90.1-2013 (Geothermal Heat Pumps < 11.25 Tons Open Loop) | MVG | 1.0
11.21.16 | Update baseline based on ASHRAE 90.1-2013 (Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX)) | MVG | 1.0
11.21.16 | Adjusted EERs of products whose baseline uses only SEER. Used formula, EER = -0.02*SEER2 + 1.12*SEER | MVG | 1.0
11.21.16 | Adjusted Heat Pump proposed efficiencies to follow CEE Tiers for "All Other" heating section instead of "Electric Resistence (None)" to match baseline | MVG | 1.0
11.21.16 | Adjusted proposed efficiencies of Ductless Mini-Splits to match with Air Cooled AC/HP <5.4 ton Split System requirements since there is no CEE tier | MVG | 1.0
11.21.16 | Adjusted Tier 0 minimum requirements to match eligibility table (includes adding SEER/IEER requirements) | MVG | 1.0
11.21.16 | Removed VRF from Tier 0 | MVG | 1.0
12.2.16 | Updated conditional formatting on Existing Equipment "SEER/IEER" column to allow for value to be entered on AC units less than 5.4 tons. Also added "(If Available)", since this is not a required field but we will use the value if it is provided | KM | draft_1.1
12.2.16 | Updated version number to draft_1.1 | KM | draft_1.1
12.2.16 | Updated effective date to 1.01.17 | KM | draft_1.1
12.13.16 | Adjusted PTAC & PTCHP size categories | KM | draft_1.2
12.15.16 | Updated version number to draft_1.2 | KM | draft_1.2
1.6.17 | Updated conditional formatting on existing equipment based on existing criteria in references tab | MVG | draft_1.3
1.6.17 | Added PTACs and PTHPs to new construction | MVG | draft_1.3
1.9.17 | Changed wording to Instruction tab step two, fourth bullet to "dark gray" | MVG | draft_1.4
1.9.17 | Updated "Equip. Status" to "Equipment Status" on Customer Inputs and Instructions tab. | MVG | draft_1.4
1.9.17 | Re-named "Total Expected Rebate Amount" to "Total Estimated Rebate Amount" on Customer Inputs tab as per Walter's request | MVG | draft_1.4
1.9.17 | Unfroze panes on "Eligibility Tab" | MVG | draft_1.4
1.10.17 | Removed SEER baseline for codes AC811/AC821 | MVG | draft_1.4
1.24.17 | Added coding to CommandButton1_Click macro to keep button size consistent | MVG | draft_1.4
1.24.17 | Added coding to checkbox1_Click macro to keep checkbox size consistent | MVG | draft_1.4
1.24.17 | Added Ts & Cs, Guidelines, Required Documents tabs | MVG | draft_1.4
1.24.17 | Updated version to 1.0 | MVG | 1.0
1.25.17 | Updated NTG values (Free Ridership, Spillover, Demand LLF, Energy LLF) to match Dimple's screenshot from e-mail sent on 1/23/17 | MVG | 1.0
5.26.17 | Changed version number to draft_2.0 and updating effective date | KM | draft_2.0
5.26.17 | Removed $/kW cap from Summary sheet. | KM | draft_2.0
6.1.17 | Updated version to 1.1 | MVG | 1.1
6.23.17 | Changed effective date to 6.26.17 | MVG | 1.1
12.21.18 | Changed Air Cooled Air Conditioner retrofit criteria for existing units from EER to IEER or IPLV for all units other than Room Air Conditioners | KM | draft_1.0
1.9.17 | Updated "Equip. Status" to "Equipment Status" on Customer Inputs and Instructions tab. | MVG | draft_1.4
1.9.17 | Re-named "Total Expected Rebate Amount" to "Total Estimated Rebate Amount" on Customer Inputs tab as per Walter's request | MVG | draft_1.4
1.9.17 | Unfroze panes on "Eligibility Tab" | MVG | draft_1.4
1.10.17 | Removed SEER baseline for codes AC811/AC821 | MVG | draft_1.4
1.24.17 | Added coding to CommandButton1_Click macro to keep button size consistent | MVG | draft_1.4
1.24.17 | Added coding to checkbox1_Click macro to keep checkbox size consistent | MVG | draft_1.4
1.24.17 | Added Ts & Cs, Guidelines, Required Documents tabs | MVG | draft_1.4
1.24.17 | Updated version to 1.0 | MVG | 1.0
1.25.17 | Updated NTG values (Free Ridership, Spillover, Demand LLF, Energy LLF) to match Dimple's screenshot from e-mail sent on 1/23/17 | MVG | 1.0
5.26.17 | Changed version number to draft_2.0 and updating effective date | KM | draft_2.0
5.26.17 | Removed $/kW cap from Summary sheet. | KM | draft_2.0
6.1.17 | Updated version to 1.1 | MVG | 1.1
6.23.17 | Changed effective date to 6.26.17 | MVG | 1.1
12.21.17 | Changed Air Cooled Air Conditioner retrofit criteria for existing units from EER to IEER or IPLV for all units other than Room Air Conditioners | KM | draft_1.0
12.22.17 | Minor edits to text | kam | draft1.1
12.22.17 | Updated macros with correct passwords and relocked all worksheets using the updated password | TM | draft_1.2
12.22.17 | Updated Existing Unit Eligibility logic in the Eff-Size Qualifications tab Columns: AE:AF. Now should correctly allow SEERs <=10.0 and EERs <= 9.0 based on the existing unit type | TM | draft_1.2
12.4.18 | Added per unit CO2 savings and per unit MMBtu savings to proposed0 tab | KM | draft_1.0
12.4.18 | Changed program year to 2019, effective date to 1.1.19 and version to daft_1.0 | KM | draft_1.0
12.6.18 | Updated eligibility date on guidelines to reflect 1.1.19 | ED | Draft_1.1
12.6.18 | Updated pseg website link on guidelines tab | ED | Draft_1.1
12.7.18 | Corrected kWh calculation to use EER for room ac instead of SEER since SEER is not available | KM | Draft_1.2
12.7.18 | Corrected baseline efficiency lookups on Proposed0 | KM | Draft_1.2
12.7.18 | Updated Line Losses to 6% Energy and 8.5% Demand | KM | Draft_1.2
12.13.18 | Updated Application Name to HVAC Rebate Application | ED | Draft_1.3
12.13.18 | Removed "Optional" from Model #/Mfg fields on worksheet | ED | Draft_1.3
12.21.19 | Updated version to 1.0 per client approval | ED | Version_1.0
2.15.19 | Added 3 columns to proposed0 tab, In Service Rate, Utility Gross kW and Utility Gross kWh | KM | draft_2.0
2.15.19 | Extended number of decimal places to 7 for kW and 5 for kWh fields on Proposed0 | KM | draft_2.0
2.15.19 | Updated Workbook name macro to account for additional columns | KM | draft_2.0
2.19.19 | Updated dropdownn selection for Package Terminal units | KM | draft_2.1
2.26.19 | Fixed Conditional Formatting logic on line 17 of the Customer Inputs tab | KM | draft_2.2
2.27.19 | Updated "existing IEER/SEER" field to include IPLV | ED | draft_2.3
2.27.19 | Updated SEER and EER examples on example line of customer inputs to reflect corrected #s based on eligiblity tablw | ED | draft_2.3
2.27.19 | Updated logo formating on all tabs | ED | draft_2.3
2.27.19 | Prop 0: Updated all savings columns to reflect "Number" format | ED | draft_2.3
3.18.19 | Updated Terms and Conditions with legal language pertaining to phone numbers | MT | draft_2.4
3.18.19 | Updated PSEGLI Logos | MT | draft_2.4
3.18.19 | Locked and hid all cells not requiring data input | MT | draft_2.4
3.18.19 | Increase row heights on Eligibility Table so all data is visible | MT | draft_2.4
3.18.19 | Updated formula in C77 on Summary tab so it properly sums values in C column above it | MT | draft_2.4
3.29.19 | Version 1.1 approved by the client and ready for release | MT | 1.1
11.11.19 | Development: Updated Version Number, Year and Effective date for 2020 Version 1 | MCR | 1.0_draft1.0
11.11.19 | References: Rearranged tables to mimic the Master Internal document | MCR | 1.0_draft1.0
11.11.19 | References: Copy pasted values from Master Internal draft 1.9.1 over tables | MCR | 1.0_draft1.0
11.11.19 | Worksheet: Unhid all Columns | MCR | 1.0_draft1.0
11.11.19 | Worksheet: Inserted column AA to Existing Equipmet table | MCR | 1.0_draft1.0
11.11.19 | Worksheet: Named new column "Heater AFUE" | MCR | 1.0_draft1.0
11.11.19 | Worksheet: Inserted Column U | MCR | 1.0_draft1.0
11.11.19 | Worksheet: Named new Column "Heating Fuel Type" | MCR | 1.0_draft1.0
11.11.19 | References: Created table in B10:B17 that includes all possible existing fuel types | MCR | 1.0_draft1.0
11.11.19 | Worksheet: Added Data validation to reference References B10:B17 | MCR | 1.0_draft1.0
11.11.19 | Worksheet: Added Conditional formatting to Existing table for HSPF, and AFUE | MCR | 1.0_draft1.0
11.15.19 | Calculations:Copy pasted 2019 Master Internal draft 1.9.1 HVAC calculations over for columns A-X | MCR | draft 2.0
11.15.19 | Calculations: Added columns AB & AC to check if calculations are using Existing or baseline conditons, and what equipemtn type that is | MCR | draft 2.0
11.15.19 | Calculations: Changed Existing/Basline to first check if a value was enetered in the existing equipment table on Customer Inputs, and if not, populate the baseline vaule from the References tab | MCR | draft 2.0
11.15.19 | Calculations: Don't allow HSPF or COP to populate if User has selected a fossil fuel baseline | MCR | draft 2.0
11.15.19 | Calculations: Added columns AN, AO, AP, AR, AS, and AT For MMBTU and BE kWh | MCR | draft 3.0
11.15.19 | Calculations: Added columns AH, AI, AJ for Existing fossil fuel equipment AFUE, Displacement, and Electric Parasitics | MCR | draft 3.0
11.15.19 | Calculations: Changed Rebate calculation to be $/kWh calculation | MCR | draft 3.0
11.18.19 | Calculations: Changed COP calculation to check References column BJ instead of BI | MCR | draft 4.0
11.18.19 | References: Updated Building types and hours to reflect Mid Atlantic TRM v9 | MCR | draft 4.0
11.18.19 | Calculations: Added formula to EFLH cooling and EFLH heating to reference the building type and references tab table | MCR | draft 4.0
11.18.19 | Customer Inputs: Added Warning over rebate columns to inform user to enter a building type | MCR | draft 4.0
11.18.19 | Calculations: Removed all reference to Eff-Q (delete) | MCR | draft 4.0
11.18.19 | Inspection Form: Changed Pre-Inspection to verify the Existing Heating Fuel instead of Unit size, and made Quantity a user entry | MCR | draft 4.0
11.18.19 | Copied Customer Inputs tab and pasted into this document | MCR | draft 5.0
11.18.19 | Small Business Heating: Renamed copied tab "Small Business Heating" | MCR | draft 5.0
11.20.19 | References: extended size category table to include ccASHPS | MCR | draft 6.0
11.20.19 | Small Business Heating: Udated Data Validation for Size Category | MCR | draft 6.0
11.20.19 | Smal Business Heating: Changed formula in Column D to not require a Sub Category to be entered | MCR | draft 6.0
11.20.19 | Calculations: Copy Pasted Customer Inouts table below it to create the Small Business Calculations table | MCR | draft 6.0
11.20.19 | Calculations: Linked the tables to the Small Business Heating tab instead of the Customer Inputs tab | MCR | draft 6.0
11.20.19 | References: Added cold climate heat pumps to the teir 1/teir2 table | MCR | draft 6.0
11.20.19 | Name Manager: Extended T1T2References Name Ranges to include new heat pump measures | MCR | draft 6.0
11.22.19 | Calculations: Extended the first Small Business Heating table to include PASS/FAIL based on Manual N inputs | MCR | draft 7.0
11.22.19 | Small Business Heating: Added columns P&Q for Manual N inputs | MCR | draft 7.0
11.22.19 | Calculations: Added final PASS/FAIL for small business heating to include if it passes the minimum requirements and is sized correctly | MCR | draft 7.0
11.22.19 | Calculations: Rebate formula for Small business heating to $/ton basis | MCR | draft 7.0
11.22.19 | Small Business Heating: Chnaged Rebate formulas to reference small business table | MCR | draft 7.0
11.22.19 | Small Business Heating: Changed the reference for the Estimate Rebate to the Claculations tab | MCR | draft 7.0
11.22.19 | Small Business heating: Changed Size (tons) and Quantity columns to be cooling btuh and heating btuh | MCR | draft 7.0
11.22.19 | Small Business heating: Added column H for AHRI Reference number | MCR | draft 7.0
11.22.19 | Small Business heating: Added integrated controls table above equipment table | MCR | draft 7.0
11.22.19 | Small Business heating: Removed customer informatin section except the building type | MCR | draft 7.0
11.22.19 | Small Business heating: Added instructions/eligibility requirements | MCR | draft 7.0
11.22.19 | Eligibility Table: Hid columns for Tier 0 and Tier 2 | MCR | draft 7.0
11.22.19 | Eligiblity Table: Changed rebates to show new $/kWh structure | MCR | draft 7.0
11.22.19 | Eligibility Table: Added Sample photos for different equipment | MCR | draft 7.0
11.22.19 | Eligibility Table: Added Small Business Whole Building Table | MCR | draft 7.0
11.22.19 | Small Business Heating: Added column AI for Contractor Incentive | MCR | draft 7.0
11.22.19 | Calculations: Added Contractor Incentive in column BJ for small business heating | MCR | draft 7.0
11.22.19 | Calculations: Only allow $500 to appear once and only for qaulified ccASHPs | MCR | draft 7.0
11.22.19 | References: Copied Integrated control info from 2019 Whole House v2.0 | MCR | draft 7.0
11.22.19 | Small Business Heating: Added data validation for integrated control list | MCR | draft 7.0
11.22.19 | Calculations: Switching calcs from ton to btu | MCR | draft 7.0
11.22.19 | Calculations: Each line should be a single heat pump. Removed quantity from Totals calcs | MCR | draft 7.0
11.22.19 | Eff-Q (delete): Deleted | MCR | draft 8.0
11.25.19 | Eligibility table: added 2 rows for each of the small business heating equipment types (ductless, ducted cold climate heat pumps) | MCR | draft 8.1
11.25.19 | Eligibility table: Added new measure codes and rebate levels for small business heating | MCR | draft 8.1
11.25.19 | Customer Inputs: Columns D & V formulas were updated to reference down to row 43 | MCR | draft 8.1
11.25.19 | Customer Inputs: Columns D & V formulas were updated to not require column E to be filled for Cold Climet heat pumps | MCR | draft 8.1
11.25.19 | References: Added new cold climate heat pump and integrated control measure codes | MCR | draft 8.1
11.25.19 | HVAC types: Added new cold climate heat pump and integrated control measure codes | MCR | draft 8.1
11.25.19 | Small Business Heating: Updated Total Savings to reference Calculations | MCR | draft 8.1
11.25.19 | Calculations: Updated Measure code formula to include cold climate heat pumps | MCR | draft 8.1
11.25.19 | Calculations: Chnaged Tier formula to only show Tier 1 when project passes and the new measure is not a cold climate heat pump | MCR | draft 8.1
11.25.19 | Summary: Added new cold cliamte measure codes | MCR | draft 8.1
12.3.19 | Changed Small Business Heating to Whole Building ccASHP | MCR | draft 8.2
12.3.19 | Whole Business ccASHP: Removed Serial Number from Integrated Controls Table | MCR | draft 8.2
12.3.19 | Whole Business ccASHP: Changed Size Category data validation to formula that always equals "All Sizes" when a ccAHP is entered | MCR | draft 8.2
12.3.19 | Whole Business ccASHP: Hid Size Category column | MCR | draft 8.2
12.3.19 | Summary: Added Totals row for WB ccASHP | MCR | draft 8.2
12.3.19 | Summary: Changed row 86 to say "HVAC Worksheet Totals" | MCR | draft 8.2
12.3.19 | Summary: Added formulas to add quanities and savings for WB ccASHP measures | MCR | draft 8.2
12.3.19 | Summary: Adjusted HVAC Worksheet Totals formulas to include new cold climate heat pumps | MCR | draft 8.2
12.3.19 | Whole Building ccASHP: Chnaged Controls Reabte to =0 when nothing is entered | MCR | draft 8.2
12.3.19 | Whole Building ccASHP: Added Integrated controls to the list of requirements | MCR | draft 8.2
12.3.19 | Whole Building ccASHP: Total estimated rebate will reference summary row 87 | MCR | draft 8.2
12.3.19 | Summary: Added check box to hide/unhide ccASHP Inspection form | MCR | draft 8.2
12.3.19 | ccASHP Inspection Form: Copies from Inspection Form | MCR | draft 8.2
12.3.19 | ccASHP Inspection Form: Linked to Whole Building ccASHP | MCR | draft 8.2
12.3.19 | ccASHP Inspection Form: Changed Post Inspection Quantity to Unit Size Heating | MCR | draft 8.2
12.3.19 | Summary tab: moved inspection check boxes to Worksheet tabs | MCR | draft 8.2
12.3.19 | Macro: Save Workbook name to references tab | MCR | draft 8.3
12.3.19 | Inspection Form: Added Workbook Name, project ID, and Additional Projects to inspect at top of form | MCR | draft 8.3
12.3.19 | ccASHP Inspection Form: Added Workbook Name, project ID, and Additional Projects to inspect at top of form | MCR | draft 8.3
12.4.19 | Whole Building ccASHP: hid contractor incentive column | MCR | draft 8.4
12.4.19 | Calculations tab: Set ccASHP Contrctor incentive to 0 | MCR | draft 8.4
12.4.19 | Eligibility Criteria: hid Contractor Incentive Column | MCR | draft 8.4
12.4.19 | Eligibility Criteria: Put Room Acs on their own table with Existing Equipment Criteria | MCR | draft 8.4
12.4.19 | References: Added Room ACS to the Tier 1 & 2 Table | MCR | draft 8.4
12.4.19 | Calculations: Added RAC only columns W & R to the HVAC Worksheet table | MCR | draft 8.4
12.4.19 | Calculations: Column W will now check if the RAC is replacing a unit <=8.0 EER, or it will FAIL | MCR | draft 8.4
12.5.19 | Calculations: Added Columns in HVAC table for Heating kW per unit and total | MCR | draft 8.5
12.5.19 | Calculations: Added Columns in HVAC table for EE and BE CO2 Savings per unit | MCR | draft 8.5
12.5.19 | Calculations: Added Columns in HVAC table for EE kWh Savings per unit | MCR | draft 8.5
12.5.19 | Calculations: Added Columns in WB ccASHP table for Heating kW per unit and total | MCR | draft 8.5
12.5.19 | Calculations: Added Columns in WH ccASHP table for EE and BE CO2 Savings per unit | MCR | draft 8.5
12.5.19 | Prop0: Added 26 rows for WB ccASHP | MCR | draft 8.5
12.5.19 | Prop0: Re-mapped HVAC and ccASHP to Prop0 | MCR | draft 8.5
12.6.19 | Calculations Shifted columns for HVAC to make room for "Existing Critera" | MCR | draft 8.6
12.6.19 | Calculations: Only allow FF MMBTU savings for HVAC replacements including a HP | MCR | draft 8.6
12.6.19 | HVAC Worksheet: Added Total MMBTU to Project Summary | MCR | draft 8.6
12.6.19 | Whole Building ccASHP: Added Total MMBTU to Project Summary | MCR | draft 8.6
12.6.19 | Cleared and locked worksheets | MCR | draft 8.6
12.6.19 | HAVC Worksheet: Added data validation to Size (Tons) based on Size Category sleected | MCR | draft 8.7
12.6.19 | Calculations: WB ccASHP table adjusted formulas for MMBTU, CO2, kW and kWh savings to not appear if product fails | MCR | draft 8.7
12.10.19 | HVAC References: ASHP >5.4 to <11.5 COP should be 3.4 | MCR | draft 8.8
12.10.19 | Whole Building ccASHP Worksheet: Added NYSERDA link for Integrated Controls | MCR | draft 8.8
12.16.19 | HVAC Worksheet: Changed existing equipment number in column V to be 2 if RAC is existing | MCR | draft 8.9
12.16.19 | Calculations: For HVAC Calcs Existing Baseline lookup starts at row 4 | MCR | draft 8.9
12.16.19 | References: Added rounding values for kW, kWh, and MMBTU | MCR | draft 8.9
12.16.19 | Calculations: Updated rounding to reference References tab | MCR | draft 8.9
12.16.19 | Eligibility table: Fixed "Busness" typo | MCR | draft 8.9
12.16.19 | Eligibility table: Wrote in "$500/project" for integrated controls incentive | MCR | draft 8.9
12.16.19 | HVAC References: Updated Dual Fuel Thermostats to include all new models | MCR | draft 8.9
12.16.19 | Eligibility Table: Added Effective Date | MCR | draft 9.0
12.16.19 | Eligibility Table: Changed Rebate on VRF to $/kWh from Tier 1 Rebate/ton | MCR | draft 9.0
12.16.19 | Calculations: Changed Rebate calculation to reference Column BJ instead of BK | MCR | draft 9.0
12.16.19 | Whole Building ccASHP: Extended the Existing Cooling drop down to 7 items in the list | MCR | draft 9.0
12.16.19 | HVAC Inputs: Extended the Existing Cooling drop down to 7 items in the list | MCR | draft 9.0
12.16.19 | Summary: Fixed CCHP211 "Total Rebate" calc | MCR | draft 9.0
12.16.19 | Whole Building ccASHP: Changed Formatting for Capacity and Manual N to Nimber with comma and no decimals | MCR | draft 9.0
12.18.19 | HVAC Worksheet: Added exapmles for existing equipment | MCR | draft 9.1
12.18.19 | Whole Building ccASHP Worksheet: Added examples for existing equipment | MCR | draft 9.1
12.18.19 | Eligibility Table: Adjusted ASHP requirements to match CEE tier requirements | MCR | draft 9.1
12.18.19 | Calculations: Updated Existing/Baseline HSPF to calculate off of COP if available (specifically for Electric resistance replacement) | MCR | draft 9.1
12.18.19 | References: Updated NTG factors | MCR | draft 9.2
12.19.19 | Whole Building ccASHP:Added AHRI ID example | MCR | draft 9.3
12.19.19 | HVAC Worksheet: Changed name range for Clear Inputs | MCR | draft 9.3
12.19.19 | Instructions Tab: Removed "And their Proposd AC equipment" and changed it to "proposed heating and cooling equipment" | ED | Draft9.4
12.19.19 | Guidelines Tab: Row 10 - Updated date to 1/1/20 | ED | Draft9.4
12.19.19 | Guidelines Tab: Row 18 - Added NEEP as approved rating agency | ED | Draft9.4
12.19.19 | Required Docs: Added a new section called "Required Documents for ccASHP Projects" - Added Manual N and AHRI as Pre-Installation required docs | ED | Draft9.4
12.19.19 | Wholle Building ccASHP Tab: Added an additional instruction to inform participant that ccASHP must be 5.4 tons or less and found on the NEEP list, also edited line 1 and removed the reference to "you" | ED | Draft9.4
12.19.19 | Instructions Tab: Changed title to say "Instructions for Completing the HVAC Worksheet" | ED | Draft9.5
1.10.20 | HAVC Worksheet: Added "(required)" under Existing Cooling and Heating Types | MCR | Draft9.8
1.10.20 | Whole Building ccASHP Worksheet: Added "(required)" under Existing Cooling and Heating Types | MCR | Draft9.8
1.12.20 | References: Updated EFLH per ODC recommendation | MCR | Draft10
1.14.20 | Worksheet Approved by client & Locked | MCR | Version 1.0
9.04.20 | References: Updated Baseline SEER/EER/IEER/HSPF/COP to be consistent with AHRAE 90.1 2016 | MCR | 2021_Version 1.0_draft1.0
References: Updated VRF Heat Pump Air Cooled Tier 1 eligibility to at least ASHRAE 2016 standards
Eligibility table: Updated minimum VRF Eligibility to match References
11.10.2020 | Calculations: added new fields for whole building calcs | MCR | Draft 1.1
11.10.2020 | References: added new fields for whole building calcs | MCR | Draft 1.1
11.11.2020 | Calculations: adjusted savings formulas to new whole building methodology in NYS TRM | MCR | Draft 1.2
11.11.2020 | Inspection Form: populated Manufacturer and Model Number for Post-Inspection | MCR | Draft 1.2
Eligibility Table: Added Row 7 under Eligibility Requirements to note that rebates are performance based and use ASHRAE as a baseline
Eligibility Table: Added Row 62 under VRFs to note that VRFs must be replacing existing multisplits
11.13.2020 | Calculations: Fixed the CO2 for regular HVAC | MCR | Draft 1.4
Eligibility Table: Expanded Integrated Controls for Whole Building
Calculations: Added Utility Gross kW Savings
Summary: Added Utility Gross kW Savings
HVAC Worksheet: Added Utility Gross kW Savings to the Project Summary
WB ccASHP Worksheet: Added Utility Gross kW Savings to the Project Summary
11.17.20 | HVAC Worksheet: Removed Utility Gross kW
WB ccASHP Worksheet: Removed Utility Gross kW Savings to the Project Summary
11.20.2020 | Eligibility Table: Added Ductless Multi-Splits to Whole Building | MCR | Draft 2.0
References: Changed Line Losses to 2021 values
12.08.20 | References: Changed the PTHP and PTAC min and Max for >=1 | MCR | Draft 2.1
12.15.20 | Customer Information: Unlocked Cell G29 | MCR | Draft 3.0
Eligibility Table: Centered Text in F36-F47
References: Fixed maximum for <11.25 <5.4 <20 & <63 to 11.2499999, 5.39999999, 19.999999, 62.99999999
12.15.20 | Ref Tab: Added tables for Organization Type and Building Type - Added to Name Manager | ED | Draft4
12.15.20 | Cust Ifno Tab: Removed Radio buttons for Org Type and Building Type- Replaced with Dropdown data validation | ED | Draft4
| Dev Tab: Updated effective date to 1.1.21 | ED | Draft4
| Guidelines Tab: Added row 8 regarding Multi-Fam Application | ED | Draft4
12.16.20 | Guidelines Tab: Removed Row 7 | MCR | draft 5.0
Required Docs: Added row above Pre-Inspection and moved Vendor's Proposal
Required Docs: Added Post Insoection box
Eligibility Table: Removed Duplicate words in instructions
Eligibility table: Changed 17 degrees to 17⁰F
Calculations: Chnaged Whold building criteria to 90% - 120%
12.28.20 | Eligibility Table: Air Cool HP 11.25 - 63 tons COP requirement changed to 3.3 COP | MCR | draft 6.0
References: Chnaged <2.5 tons to Max of 2.499999
Calculations: Existing Baselin COP Reference search expanded to 4:44
Calculations: Cooling kWh rounding using SEER now also references the references tab
Calculations: Heating kW was missing kW increase if Proposed COP is present and baseline is not
References: Added "Existing Other" as abseline with electric CO2
WB cc ASHP Worksheet: Corrected spelling error in Existing Equipmet warning in column AM
References: Removed "Control from Dual fuel Thermostat ccASHP scenario look up name
References: Added the word "Capacity" to the Integrated/Fixed ccASHP scenario look up name
Calculations: For HP Sizing Ratio "OR" statement was added to include both Integrated/Modulating and No Fossil Fuel Heating
References: Double checked ASHRAE 2016 Baselines
12.29.20 | Summary: Added new IC measure codes | MCR | draft 7.0
Summary: expanded Sum for Whole Building
12.30.20 | Locked and finalized for Jan 2021 Launch | ED | Version1.0
Ventilation Worksheet
2021-04-05 | Added Ventilation measure in Eligibility table | RS | Version1.0
2021-04-05 | Added measure codes for ventilation measures | RS | Version1.0
2021-04-07 | Created Ventilation worksheet and Added ventilation measures into it | RS | Version1.0
2021-04-14 | In reference tab added relevent reference of ventilation measures from cell D146 | RS | Version1.0
2021-04-16 | In Calculation tab added ventilation measures calcs from cell C67 | RS | Version1.0
2021-04-27 | Fixed the calcs and formatting of Ventilation tab and calcualtion tab. | RS | Version1.0
2021-04-28 | In summary tab added Ventilation measures from Cell C91 | RS | Version1.0
2021-05-03 | Created Ventilation Inspection Forms | RS | Version1.0
2021-05-13 | Summary: Added IFNA to IC measure codes | MCR | Version1.1_draft4
2021-06-07 | Summary: Changed measure codes to match internal | MCR | draft8
2021-06-08 | Inspection Forms: Added COVID-19 questions | MCR | draft9
2021-06-15 | Calculations: Changed The Depth reference to the ventilation tab to column G | MCR | draft 10
Calculations: Changed the Fan kWh savings to divide by the unit quantity to get per unit savings
Summary: Hnaged the Total and per unit references for ventilation and fans
2021-06-21 | Dev Tab: Updated version to 2.0 and effective date to 7.5.21 | ED | Draft11
Summary Tab: Updated new measures codes to reflect V100, V110, and V200
Ventilation Tab: Updated formatting for all numeric fields
Elig TableTab: Updated new measures codes to reflect V100, V110, and V200
HVLS INS Tab: Fixed Qty formula for Post INS section
2021-06-23 | Calculations: Removed CF from HVLS fan Peak Summer kW | MCR | Draft 12
Summary tab: Switched per unit and total for ERVs and HRVs
Summary tab: Added Sumif to all ventilation measures
2021-06-24 | Calculations: Removed CF from ERV and HRVs | MCR | Draft 13
Ventilation: Change Total Per Unit to Total Cost
2021-06-28 | Ref Tab: Added Name Manager Functions for "Existing Fan Type" "Fan Building Type" and "Fan Type" | ED | Draft15
| Ventilation Tab: Added data validation with Name Manager to Existing Fan Type, Fan Building Type, and Fan Type dropdown fields | ED | Draft15
| Ven Tab: Corrected typos in 70% cost cap message | ED | Draft15
| Summary Tab: Added rows for ventilation to Total Rebate and Total MMBTU formulas | ED | Draft15
| Cals Tab: Added Utility Gross kW fields to columns AJ and AV for the ERVs and HRVs - Added formulas | ED | Draft15
| Cals Tab: Added Utility Gross kW fields to columns T for the Fans - Added formulas | ED | Draft15
| Summary Tab: Added UG kW columns from ERV/HRV/FANs sections on Calcs tab to rollup to Total Utility Gross kW formula on Summary Tab | ED | Draft15
Veniliation Tab: Added Name Manager "ERVHRV_Info" and "Fan_Info" to clear contents linked to Clear Inputs Tab - Updated Code to account for this
10.18.21 | Development tab: Unlocked for 2022 changes | MCR | Draft1
11.8.21 | References: Edited the CO2 values for electric | MCR | Draft2
Guidelines: Added language regaurding rebates from multiple utilities and other entities
11.15.21 | Guidelines: Changed submit after date to January 1,2022 | MCR | Draft 3
Worksheet: Dragged up formula in column D
11.18.21 | Customer Information: Added New Construction and Existing Building to the drop down | MCR | Draft4
12.07.21 | Customer Information: Unlocked and Unhide Project Type | MCR | Draft 5
Customer Information: Chnaged Building Type drop down to reference the same as the Worksheet tab
HVAC Inputs: Changed Building Type to formula to match Customer Info tab
Whole Building ccASHP: Chnaged Building Type to match Customer Info tab
Summary: Updated MMBTU per unit to Total MMBTU/Quantity
12.29.21 | Locked worksheet for Launch | MCR
6.8.22 | Eligibility Table: Hid VRF table | MCR | Version 2.0_draft1
Eligibility Table: Added Information about Whole Building and VRF being moved to custom and the NYS Clean Heat Calc
6.9.22 | Eligibility Table: Adjusted language regarding VRFs | MCR | draft2
7.1.22 | References: Removed VRF from Existing Building and NC equipment drop downs | MCR | draft3
HVAC Worksheet: Adjusted Data Validation for Equipment drop down to reference new data ranges
Whole Building ccASHP: Made sheet very hidden
Eligibility Table: Adjusted Whole Building language
Eligibility Table: Removed Whole Building ccASHP table
7.5.22 | Dev Tab: Updated version number to reflect 2.0 | AW | Draft 3
7.5.22 | Required Documents: Removed Whole Building specific documents | MCR | Draft 4
7.7.22 | Locked and finalized for launch | MCR | Version 2.0
8.5.22 | Whole Building ccASHP: Removed remaining data entered | MCR | Version 2.1_draft1
Summary: ccASHP WB measures were removed from the summary table
8.26.22 | Locked for Version 2.1 | MCR | Version 2.1
10.12.22 | Develpement: Updated Year and Version for 2023 Version 1.0 | MCR | Version1.0_draft1
11.18.22 | Develpement: changed effective date | MCR | draft2
Guidelines: Updated naming convention for 23
References: Added cloumn for New Construction Baseline
11.21.22 | References: Changed New Construction to "Baseline New Construction" | MCR | draft3
Calculations: Added "Baseline New Constrution" to BE savings calcs
Eligibility Table: Removed Eco Dev Room Air Conditioners
Eligibility Table: Removed unused columns
Customer Information: Added Rebate Payment Method drop down & removed check box
References: Added Rebate payment drop down options
12.13.22 | References: Removed "kWh" from cell G139 | MCR | draft4
Calculations: Highlighted AFUE column to note changes
References: Removed Room Air Conditioner from Existing Building Drop Down
HVAC Worksheet: Chnaged Equipment Type Drop Down to always equal References Column D (No Eco Dev)
References: Updated Baseline SEER, EER, and HSPF values for systems <5.4 tons to new 2023 Standards
12.20.22 | Eligibility Table: Updated Heat Pump incentives to $2.00/kWh per approved memo | MCR | draft5
References: Updated Heat Pump incentives 10 $2.00/kWh per approved memo
12.27.22 | HVAC Types: Added Multi Split CCHP | ED | Draft 6
References: Added Multi Split CCHP All Types
HVAC Worksheet: Updated Data Validation for Sub Caegory dropdown to accommodate Multi Split CCHP
12.28.22` | HVAC References: Updated baseline data back to match 2023 DSA TRM - We are awaiting updated CEE Guidance for Efficiency values (Mid 2023) - Once we have that guidance, we will update baselines back to 2023 Code | ED | Draft7
Summary Tab: Updated formulas for Total Savings to include ccASHP measures
Calcs Tab: Corrected UG kW formula to include Multi Splits
1.10.23 | Locked and final per client approval | ED | V1
2023-09-28 | Dev Tab: Updated Program Year to 2023, Current Effective Date to 1.1.24 | EM | V1
Updated all Tabs with new color of Dark Steel Gray and new PSEG logo
10.5.23 | References:
Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons: (baselines) EER 11 -> 12.1; IEER 12.7 -> 14.6
Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons: (Baselines) EER 10.8 -> 11.8; IEER 12.2 -> 14.0
Air Conditioners - Air Cooled ≥ 20 & < 63 Tons: (Baselines) EER 9.8 -> 11.2; IEER 11.4 -> 13
Air Cooled Heat Pumps ≥ 5.4 & < 11.25 Tons: (Baselines) EER 10.8 -> 11.7; IEER 12 -> 13.9; COP 3.3 -> 3.4
Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons: (Baselines) EER 10.4 -> 11.4; IEER 11.4 ->13.3; COP 3.2 -> 3.3
Air Cooled Heat Pumps ≥ 20 & < 63 Tons: (Baselines) EER 9.3 -> 10.8; IEER 10.4 -> 12.3
Ductless Mini-Split AC < 5.4 tons All Types: (Baselines) EER 11.18 -> 11.2
Ductless Mini-Split Heat Pumps < 5.4 tons All Types: (Baselines) EER 11.76 -> 11.2; SEER 14->13
VRF Water Source Heat Pumps < 11.25 Tons Multisplit System: (Baselines) IEER n/a -> 16
Cold Climate Air Source Heat Pumps All Sizes All Types: (Baselines) EER 11.76 -> 11.8
| GEO All types: (Baselines) EER 10.8 -> 11.2 | SB | V1_D2
10.6.23 | References:
ERV/HRV: Toutdoor, heating: 45.93 -> 53.2
Operating Days:
24/7 - 365: Cooling 2863 -> 2684; Heating 5735 -> 5920
Mon - Sun 6AM-12AM: Cooling 2400 ->2152; Heating 4409 -> 4303
Mon - Sun 6AM-10PM: Cooling 2057 ->1946; Heating 3673 -> 3796
Mon - Fri 7AM-7PM and Sun 11AM-6PM: Cooling 1547 ->1220; Heating 2602 -> 2204
Mon - Fri 7AM-7PM: Cooling 1334 ->1081; Heating 2347 -> 1984
Mon - Fri 7AM-5PM: Cooling 1046 ->890; Heating 1779 -> 1663
Other: Avg of above values
HVLS:
Oper Hours: 5162 -> 4988
| Saving Calcs updated as per 2024 DSA TRM | SB | V1_D3
10.9.23 | References:
BEFLH:
Updated to Reflect NYS TRM V10 Appendix G
| Large Comercial category using CAV nonecon | SB | V1.D4
10.31.23 | References:
Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons: ( Eff baselines) EER 12 -> 12.6; IEER 14.6 -> 17, Tier II EER 12.4 -> 12.6
Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons: (Eff Baselines) EER 12 -> 12.3; IEER 14 -> 16.5, Tier II EER 12 -> 12.3
Air Conditioners - Air Cooled ≥ 20 & < 63 Tons: (Eff Baselines) EER 10.6 -> 11.5; IEER 13 -> 16
Air Cooled Heat Pumps ≥ 5.4 & < 11.25 Tons: (Eff Baselines) EER 11.6 -> 12.1; IEER 13.4 -> 14.5 COP 3.4 -> 3.5
Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons: (Eff Baselines) EER 10.7 -> 12.4; IEER 12.6 ->13.9; COP 3.3 -> 3.4
Air Cooled Heat Pumps ≥ 20 & < 63 Tons: (Eff Baselines) EER 10.1 -> 11.8; IEER 11.6 -> 12.9
| New Eff baselines from file name "New HVAC Eff Baselines Analysis" in 2024 Drafts HVAC Folder | SB | V1.D6
11.3.23 | Worksheet Tab: Remove "Room" 2 clause from column V to properly calculate Room AC as existing condition savings | ED | V1_D8
11.6.23 | Final and locked per Client Approval | SB | V1
12.28.23 | Created V2.0_Draft1 | ED | V2-D1
Guidelines Tab: Added language that all whole building heat pumps should go Custom
Eligibility Table Tab: Added language that all whole building heat pumps should go Custom and rebates are for Partial Heat Pumps House
11.18.23 | Final and locked per Client Approval | SB | V2.0
3.12.24 | Whole Build ccASHP Tab: Unhid tab and renamed to Part Building Heat Pump Tab | ED | V3_Draft1
Req Docs: Added Part Building Required Docs
Eligibility Table Tab: Unhid Whole Building Table and renamed to Part Building - Updated efficiency to be "Must be on NEEP List"
3.20.24 | Name Manager: Updates Name Manager for Equipment Dropdown on HVAC Worksheet to exclude ccASHP | ED | V3_Draft2
Name Manager: Updated Name Manager on Part Building ccASHP Worksheet to reflect ccASHP only
|  | ED | Ve_Draft6
3.26.24 | Ref Tab: Updated Controls section to be just Separate Control
Calcs Tab: Updated formulas accordingly for Separate controls
Sumamry Tab: Updated formulas to link to Small Biz heating table
3.27.24 | HVAC Tab: Hid all heat pumps except PTHP | ED | V3_Draft9
Ref Tab: Updated PTHP rebate to 750/Ton
Calcs Tab: updated rebate calcs to calculate PTHP at $/Ton rebate, all other rebates from HVAC Worksheet Tab to remain at $/kWh
Part Build Tab: Removed AHRI references and replaced with NEEP refeeences
Part Build Tab: Removed Small Business in tab name
Part Build Tab: Added data validation for systems over 300,000 17F heating BTU
Elig Tab: Removed all non CC heat pumps
Elig Tab: Updated % load for ccSHP to 65-135%
Elig Tab: Updated PTHP rebate to $750/Ton
3.27.24 | Ref Tab: Updated all heat pump rebates to $600/Ton | ED | V3_Draft10
Elig Tab: Updated all heat pump rebates to reflect $600/Ton
4.16.24 | Cust Info Tab: Added dropdown for DAC Yes/No with link to NYSERDA Page | ED | V3_Draft12
Ref Tab: Added Table and Name Manager for DAC Yes/No
Eligibility Table Tab: Updated Part Building Rebate Structure to reflect 600/ton, 750/Ton (Bonus Rebate), 900/Ton DAC Bonus Rebate
Calcs Tab: Updated Rebate formula to calculate based on Bonus Rebate and DAC Rebate
Eligibility Table Tab: Added language regarding updated rebates and eligibility (Submitted after 4/1/24, and closing docs received by 11/1/24
4.3 | Locked and Final per Client Approval | ED | V3
Note on C354: Rush, Meaghan: May have to be changed.

## References (hidden)
*Add note about where we got % from | [33 empty] | Tier 0 | [9 empty] | Sources: 2024 PSEG LI TRM - For Updated Efficient Data - Data based on historical Captures data | [17 empty] | Integrated Controls
| Equipment Type - Sub Categories | [15 empty] | Existing Unit - Equipment Type | [11 empty] | Code Lookup |  |  |  |  | Efficiency Requirements | New Unit (min) |  |  |  |  | Existing Unit (max) |  |  |  | Efficiency Requirements | Tier 1 |  |  |  |  | Tier 2 | [6 empty] | Baseline |  |  |  |  | Which one is installed?
| Room Air Conditioners | Ductless Mini-Split AC | Air Conditioners - Air Cooled | Air Conditioners - Water & Evaporatively Cooled | Geothermal Heat Pumps | Ductless Mini-Split Heat Pumps | Air Cooled Heat Pumps | Water Source Heat Pumps | VRF Air Cooled Heat Pumps | VRF Water Source Heat Pumps | Packaged Terminal Air Conditioners | Packaged Terminal Heat Pumps | Cold Climate Air Source Heat Pumps | Ductless Mini-Split Cold Climate Heat Pumps | Ductless Multi-Split Cold Climate Heat Pumps |  | Condition | Proposed criteria | Existing Criteria | Baseline Cooling Equipement | Baseline Heating Equipement | Existing Equipment Dropdown List | [6 empty] | Equipment | Code | Product Line | Product Class | Product Name |  | SEER | EER | HSPF | COP | Rebate* | SEER | EER | HSPF | COP |  | IEER | EER | HSPF | COP | Rebate* | SEER | EER | HSPF | COP | Enhanced rebate 1 | Enhanced rebate 2 | Enhanced rebate 3 | IEER/SEER | EER | HSPF | COP |  | Dual Fuel Thermostat |  | Model Names
[17 empty] | Room Air Conditioners < 2.5 Tons All Types | 2 | 2 | Room Air Conditioner | None |  | Room Air Conditioner | None |  |  |  |  | Room Air Conditioners < 2.5 Tons All Types Tier 0 | AC100 | Cooling - HVAC Equipment | Air Conditioners | ACR Room Air Conditioners - AC100 | Room Air Conditioners < 2.5 Tons All Types Room Air Conditioner |  | 10.4 |  |  | 200 | N/A | 8 | N/A | N/A | Room Air Conditioners < 2.5 Tons All Types |  | 10.4 |  |  | 0.55 | [12 empty] | Integrated/Modulating Control |  | Aprilaire | Bosche | Bryant | Building36 | Carrier | Ecobee | Honeywell Home | Lennox Industries Inc. | LG Electronics | Nest | Nexia | Robertshaw | Tekmar
| All Types | All Types | Split System | Split System | Closed Loop | All Types | Split System | All Types | Multisplit System | Multisplit System | All Types | All Types | All Types | All Types | All Types |  | Ductless Mini-Split AC < 5.4 Tons All Types | 1 | 1 | Ductless Mini-Split AC | None |  | Room Air Conditioner | Ductless Mini-Split AC | None |  |  |  | Ductless Mini-Split AC < 5.4 Tons All Types Tier 0 | AC200 | Cooling - HVAC Equipment | Air Conditioners | ACR Ductless Mini Split - AC200 | Ductless Mini-Split AC < 5.4 Tons All Types Room Air Conditioner | 15 | 12.5 |  |  | 600 | N/A | 8 | N/A | N/A | Ductless Mini-Split AC < 5.4 tons All Types | 15 | 12.5 |  |  | 0.55 | 16 | 13 |  |  | 230 |  |  | 13 | 11.2 |  |  |  | Integrated/Fixed Capacity Control |  | 8446 | Bosch Connected Control BCC100 Thermostat | Evolution System Control | Intelligent Thermostat | COR | Ecobee 3 lite | Prestige IAQ | iComfort E30 | Thermostat | Nest Third Gen | Trane/American Standard/Service First | Robertshaw | Invita
|  |  | Single Package | Single Package | Open Loop |  | Single Package | [9 empty] | Air Conditioners - Air Cooled < 5.4 Tons Split System | 1 | 1 | Air Conditioner Split System | None |  | Room Air Conditioner | Split System AC | None |  |  |  | Ductless Mini-Split AC < 5.4 Tons All Types Tier 1 | AC201 | Cooling - HVAC Equipment | Air Conditioners | ACR Ductless Mini-Split AC - AC201 | Ductless Mini-Split Heat Pumps < 5.4 Tons All Types Room Air Conditioner | 15 | 12.5 | 8.5 |  | 600 | N/A | 8 | N/A | N/A | Air Conditioners - Air Cooled < 5.4 Tons Split System | 16 | 13 |  |  | 0.55 | 18 | 13 |  |  | 230 |  |  | 13 | 11.18 |  |  |  | No Fossil Fuel Heating |  | 8448 |  | COR |  | COR 5C | Ecobee 4 | Smart Round | iComfort M30
Worksheet Name |  |  |  |  | Direct Exchange (DX) | [11 empty] | Air Conditioners - Air Cooled < 5.4 Tons Single Package | 1 | 1 | Air Conditioner Single Package | None |  | Room Air Conditioner | Single Package AC | None |  |  |  | Ductless Mini-Split AC < 5.4 Tons All Types Tier 2 | AC202 | Cooling - HVAC Equipment | Air Conditioners | ACR Ductless Mini-Split AC - AC202 | Air Conditioners - Air Cooled < 5.4 Tons Split System Room Air Conditioner | 16 | 13 |  |  | 300 | N/A | 9 | N/A | N/A | Air Conditioners - Air Cooled < 5.4 Tons Single Package | 16 | 12 |  |  | 0.55 | 17 | 12.5 |  |  | 230 |  |  | 14 | 11.76 | [5 empty] | 8476 |  | COR 5C |  | COR 7C | Ecobee Smart Thermostat with Voice Control | T6 Pro | iComfort S30
PSEGLI_2023 HVAC Worksheet_VERSION 1.0.xlsm | [16 empty] | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System | 1 | 1 | Air Conditioner Split System | None |  | Room Air Conditioner | Split System AC | None |  |  |  | Air Conditioners - Air Cooled < 5.4 Tons Split System Tier 0 | AC310 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC310 | Air Conditioners - Air Cooled < 5.4 Tons Split System Split System | 16 | 13 |  |  | 300 | 10 | 9.4 | N/A | N/A | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System | 17 | 12.6 |  |  | 0.55 | 17.8 | 12.6 |  |  | 110 |  |  | 14.6 | 12.1 |  |  |  | Manufacturers |  | 8600 |  | COR 7C |  | Infintiy System Control |  | T6 Pro Smart | iComfort WiFi
| Equipment Type - Size Categories | [15 empty] | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package | 1 | 1 | Air Conditioner Single Package | None |  | Room Air Conditioner | Split System AC | Single Package AC | None |  |  | Air Conditioners - Air Cooled < 5.4 Tons Split System Tier 1 | AC311 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC311 | Air Conditioners - Air Cooled < 5.4 Tons Single Package Room Air Conditioner | 16 | 12 |  |  | 300 | N/A | 9 | N/A | N/A | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package | 17 | 12.6 |  |  | 0.55 | 17.8 | 12.6 |  |  | 110 |  |  | 14.6 | 12.1 |  |  |  | Dual Fuel Thermostat | Integrated Control | 8620 | [5 empty] | VisionPro 800 Smart
Heating Fuels | Room Air Conditioners | Ductless Mini-Split AC | Air Conditioners - Air Cooled | Air Conditioners - Water & Evaporatively Cooled | Geothermal Heat Pumps | Ductless Mini-Split Heat Pumps | Air Cooled Heat Pumps | Water Source Heat Pumps | VRF Air Cooled Heat Pumps | VRF Water Source Heat Pumps | Packaged Terminal Air Conditioners | Packaged Terminal Heat Pumps | Cold Climate Air Source Heat Pumps | Ductless Mini-Split Cold Climate Heat Pumps | Ductless Multi-Split Cold Climate Heat Pumps |  | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System | 1 | 1 | Air Conditioner Split System | None |  | Room Air Conditioner | Split System AC | Single Package AC | None |  |  | Air Conditioners - Air Cooled < 5.4 Tons Split System Tier 2 | AC312 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC312 | Air Conditioners - Air Cooled < 5.4 Tons Single Package Single Package | 16 | 12 |  |  | 300 | 10 | 9.4 | N/A | N/A | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System | 16.5 | 12.3 |  |  | 0.55 | 16.8 | 12.3 |  |  | 100 |  |  | 14 | 11.8 |  |  |  | Aprilaire | Carrier | 8910 | [5 empty] | VisionPro 800 Smart
Electric | [16 empty] | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package | 1 | 1 | Air Conditioner Single Package | None |  | Room Air Conditioner | Split SystemAC | Single Package AC | None |  |  | Air Conditioners - Air Cooled < 5.4 Tons Single Package Tier 0 | AC320 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC320 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System Room Air Conditioner | 13.8 | 12 |  |  | 400 | N/A | 9 | N/A | N/A | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package | 16.5 | 12.3 |  |  | 0.55 | 16.8 | 12.3 |  |  | 100 |  |  | 14 | 11.8 |  |  |  | Bosche | CMNA ICP-MIDEA | 8476W | [5 empty] | WiFi 8000
Gas | < 2.5 Tons | < 5.4 Tons | < 5.4 Tons | All Sizes | < 11.25 Tons | < 5.4 Tons | < 5.4 Tons | < 11.25 Tons | < 5.4 Tons | < 11.25 Tons | < 0.75 Tons | < 0.75 Tons | All Sizes | All Sizes | All Sizes |  | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System | 1 | 1 | Air Conditioner Split System | None |  | Room Air Conditioner | Split SystemAC | Single Package AC | None |  |  | Air Conditioners - Air Cooled < 5.4 Tons Single Package Tier 1 | AC321 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC321 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System Split System | 13.8 | 12 |  |  | 400 | 10.3 | 10.1 | N/A | N/A | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System | 16 | 11.5 |  |  | 0.55 | 16.5 | 11.8 |  |  | 90 |  |  | 13 | 11.2 |  |  |  | Bryant | Daikin | 8620W | [5 empty] | True Zone Dual Fuel Zoning Panel Kit
Oil |  |  | ≥ 5.4 & < 11.25 Tons |  |  |  | ≥ 5.4 & < 11.25 Tons |  | ≥ 5.4 & < 11.25 Tons |  | ≥ 0.75 Tons & < 1 Ton | ≥ 0.75 Tons & < 1 Ton |  |  |  |  | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package | 1 | 1 | Air Conditioner Single Package | None |  | Room Air Conditioner | Split System AC | Single Package AC | None |  |  | Air Conditioners - Air Cooled < 5.4 Tons Single Package Tier 2 | AC322 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC322 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System Single Package | 13.8 | 12 |  |  | 400 | 10.3 | 10.1 | N/A | N/A | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package | 16 | 11.5 |  |  | 0.55 | 16.5 | 11.8 |  |  | 90 |  |  | 13 | 11.2 |  |  |  | Building36 | EWC Controls | 8910W | [5 empty] | True Zone Dual Fuel Zoning Panel
Propane |  |  | ≥ 11.25 & < 20 Tons |  |  |  | ≥ 11.25 & < 20 Tons |  | ≥ 11.25 & < 20 Tons |  | ≥ 1 Tons | ≥ 1 Tons |  |  |  |  | Air Conditioners - Air Cooled ≥ 63 Tons Split System | 1 | 1 | Air Conditioner Split System | None |  | Room Air Conditioner | Split System AC | Single Package AC | None |  |  | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System Tier 0 | AC410 | Cooling - HVAC Equipment | Air Conditioners | ACR Packaged Air Conditioner - AC410 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System Other | 13.8 | 12 |  |  | 400 | 10.3 | 10.1 | N/A | N/A | Air Conditioners - Air Cooled ≥ 63 Tons Split System | 11.4 | 9.7 |  |  | 0.55 | 12.1 | 10.2 |  |  | 50 |  |  | 11 | 9.5 |  |  |  | Carrier | Fujitsu | 8920W
Other |  |  | ≥ 20 & < 63 Tons |  |  |  | ≥ 20 & < 63 Tons |  | ≥ 20 Tons | [7 empty] | Air Conditioners - Air Cooled ≥ 63 Tons Single Package | 1 | 1 | Air Conditioner Single Package | None |  | Room Air Conditioner | Split System AC | Single Package AC | None |  |  | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System Tier 1 | AC411 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC411 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package Room Air Conditioner | 13.8 | 12 |  |  | 400 | 10.3 | 10.1 | N/A | N/A | Air Conditioners - Air Cooled ≥ 63 Tons Single Package | 11.4 | 9.7 |  |  | 0.55 | 12.1 | 10.2 |  |  | 50 |  |  | 11 | 9.5 |  |  |  | Ecobee | Gree | 8800
None | [16 empty] | Air Conditioners - Water & Evaporatively Cooled All Sizes Split System | 2 | 2 | Air Conditioner Split System | None |  | Split System AC | Single Package AC | None |  |  |  | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Split System Tier 2 | AC412 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC412 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package Split System | 13.8 | 12 |  |  | 400 | 10.3 | 10.1 | N/A | N/A | Air Conditioners - Water & Evaporatively Cooled All Sizes Split System |  | 14 |  |  | 0.55 | N/A | N/A | N/A | N/A | N/A |  |  |  | 12.1 |  |  |  | Honeywell Home | Haier | 8810
[17 empty] | Air Conditioners - Water & Evaporatively Cooled All Sizes Single Package | 2 | 2 | Air Conditioner Single Package | None |  | Split System AC | Single Package AC | None |  |  |  | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package Tier 0 | AC420 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC420 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package Single Package | 13.8 | 12 |  |  | 400 | 10.3 | 10.1 | N/A | N/A | Air Conditioners - Water & Evaporatively Cooled All Sizes Single Package |  | 14 |  |  | 0.55 | N/A | N/A | N/A | N/A | N/A |  |  |  | 12.1 |  |  |  | Lennox Industries Inc. | LG Electronics | 8820
[17 empty] | Ductless Mini-Split Heat Pumps < 5.4 tons All Types | 4 | 3 | Ductless Mini -Split Heat Pumps | New Construction |  | Room Air Conditioner | Ductless Mini-Split AC | Ductless Mini-Split HP | None |  |  | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package Tier 1 | AC421 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC421 | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package Other | 13.8 | 12 |  |  | 400 | 10.3 | 10.1 | N/A | N/A | Ductless Mini-Split Heat Pumps < 5.4 tons All Types | 15 | 12.5 | 8.5 |  | 2 | 16 | 13 | 9 |  | 230 |  |  | 13 | 11.2 | 8.2 | 2.4033 |  | LG Electronics | Mitsubishi Electric | 8830
Peak Emmision Factor | Drop Down Lists |  |  |  | NYS TRM V10 | NYS TRM V10 |  | Size Requirements | [8 empty] | Air Cooled Heat Pumps < 5.4 Tons Split System | 4 | 3 | Air Cooled Heat Pumps Split System | New Construction |  | Split System AC | Split System HP | None |  |  |  | Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons Single Package Tier 2 | AC422 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC422 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System Room Air Conditioner | 2 | 11.5 |  |  | 400 | N/A | 9 | N/A | N/A | Packaged Terminal Air Conditioners < 0.75 Tons All Types |  | 12.2 |  |  | 0.55 | N/A | N/A | N/A | N/A | N/A |  |  |  | 14 |  |  |  | Nest | Samsung Electric | 8840
(lb CO2 / Unit) | Equipment Type (Existing) | Equipment Type (New Construction) | Manufacturer | Building Type | Cooling ELFH | Heating EFLH |  | Range | Minimum | Maximum |  |  | Key: |  |  |  | Air Cooled Heat Pumps < 5.4 Tons Single Package | 4 | 3 | Air Cooled Heat Pump Single Package | New Construction |  | Single Package AC | Single Package HP | None |  |  |  | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System Tier 0 | AC510 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC510 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System Split System | 13 | 12 |  |  | 400 | 9.7 | 9.5 | N/A | N/A | Packaged Terminal Air Conditioners ≥ 0.75 Tons & < 1 Ton All Types |  | 11.4 |  |  | 0.55 | N/A | N/A | N/A | N/A | N/A |  |  |  | 14 |  |  |  | Nexia | Panasonic
1.341 | Air Conditioners - Air Cooled | Ductless Mini-Split AC | AAON, INC. | Select … |  |  |  | < 0.75 Tons | 0 | 0.75 |  |  | 1 | EER, SEER or IEER |  |  | Air Cooled Heat Pumps ≥ 5.4 & < 11.25 Tons Split System | 3 | 3 | Air Cooled Heat Pumps Split System | New Construction |  | Split System AC | Single Package AC | Split System HP | Single Package HP | None |  | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System Tier 1 | AC511 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC511 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System Single Package | 13 | 12 |  |  | 400 | 9.7 | 9.5 | N/A | N/A | Packaged Terminal Air Conditioners ≥ 1 Tons All Types |  | 10.4 |  |  | 0.55 | N/A | N/A | N/A | N/A | N/A |  |  |  | 14 |  |  |  | Robertshaw | Any IR Controlled Mini-split + Flair
| Air Conditioners - Water & Evaporatively Cooled | Air Conditioners - Air Cooled | AEROSYS, INC. | Assembly | 621 | 588 |  | ≥ 0.75 Tons & < 1 Ton | 0.75 | 0.99999 |  |  | 2 | EER only |  |  | Air Cooled Heat Pumps ≥ 5.4 & < 11.25 Tons Single Package | 3 | 3 | Air Cooled Heat Pump Single Package | New Construction |  | Split System AC | Single Package AC | Split System HP | Single Package HP | None |  | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System Tier 2 | AC512 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC512 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Split System Other | 13 | 12 |  |  | 400 | 9.7 | 9.5 | N/A | N/A | Air Cooled Heat Pumps < 5.4 Tons Split System | 15 | 12.5 | 8.5 |  | 2 | 16 | 13 | 9 |  | 230 |  |  | 14 | 11.76 | 8.2 | 2.4033 |  | Tekmar
Off-PeakEmmision Factor | Ductless Mini-Split AC | Air Conditioners - Water & Evaporatively Cooled | AIR GREEN CORPORATION | Auto Repair | 395 | 1863 |  | ≥ 1 Tons | 1 | None |  |  | 3 | EER, SEER or IEER and COP |  |  | Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Split System | 3 | 3 | Air Cooled Heat Pumps Split System | New Construction |  | Split System AC | Single Package AC | Split System HP | Single Package HP | None |  | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package Tier 0 | AC520 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC520 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package Room Air Conditioner | 13 | 12 |  |  | 400 | 9.7 | 9.5 | N/A | N/A | Air Cooled Heat Pumps < 5.4 Tons Single Package | 15 | 12 | 8.2 |  | 2 | 16 | 12 | 8.2 |  | 230 |  |  | 14 | 11.76 | 8 | 2.3447 | *Using 47°F DB / 43°F WB |  |  | Model Numbers
(lb CO2 / Unit) | Packaged Terminal Air Conditioners | Ductless Mini-Split Heat Pumps | AIR-CON INTERNATIONAL, INC. | Big Box Retail | 1187 | 186 |  | < 5.4 Tons | 0 | 5.4 |  |  | 4 | EER, SEER or IEER and HSPF |  |  | Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Single Package | 3 | 3 | Air Cooled Heat Pump Single Package | New Construction |  | Split System AC | Single Package AC | Split System HP | Single Package HP | None |  | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package Tier 1 | AC521 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC521 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package Split System | 13 | 12 |  |  | 400 | 9.7 | 9.5 | N/A | N/A | Air Cooled Heat Pumps ≥ 5.4 & < 11.25 Tons Split System | 14.5 | 12.1 |  | 3.5 | 2 | N/A | N/A | N/A | N/A | N/A |  |  | 13.9 | 11.7 |  | 3.4 |  | Based on list above. If not on list above, it will not be counted. |  | Aprilaire | Bosche | Bryant | Building36 | Carrier | Ecobee | Honeywell Home | Lennox Industries Inc. | LG Electronics | Nest | Nexia | Robertshaw | Tekmar
1.1962 | Packaged Terminal Heat Pumps | Air Cooled Heat Pumps | AIREASE | Community College | 1128 | 1286 |  | < 2.5 Tons | 0 | 2.5 |  |  | 5 | EER and COP |  |  | Air Cooled Heat Pumps ≥ 20 & < 63 Tons Split System | 3 | 3 | Air Cooled Heat Pumps Split System | New Construction |  | Split System AC | Single Package AC | Split System HP | Single Package HP | None |  | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package Tier 2 | AC522 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC522 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package Single Package | 13 | 12 |  |  | 400 | 9.7 | 9.5 | N/A | N/A | Air Cooled Heat Pumps ≥ 5.4 & < 11.25 Tons Single Package | 14.5 | 12.1 |  | 3.5 | 2 | N/A | N/A | N/A | N/A | N/A |  |  | 13.9 | 11.7 |  | 3.4 |  | Model | Capability | 8446 | BCC100 | SYSTXBBECC01 | B36-T10 | T6-WEM01-A | EB-STATE3LT*** | YTHX9421R5085WW | E30 | PREMTVBC0 | T3008US | ACONT824AS52D* | 9725I2 | 564
|  | Water Source Heat Pumps | AIRE-FLO | Fast Food Restaurant | 598 | 793 |  | < 11.25 Tons | 0 | 11.25 |  |  | 6 | All |  |  | Air Cooled Heat Pumps ≥ 20 & < 63 Tons Single Package | 3 | 3 | Air Cooled Heat Pump Single Package | New Construction |  | Split System AC | Single Package AC | Split System HP | Single Package HP | None |  | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System Tier 0 | AC610 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC610 | Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons Single Package Other | 13 | 12 |  |  | 400 | 9.7 | 9.5 | N/A | N/A | Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Split System | 13.9 | 12.4 |  | 3.4 | 2 | N/A | N/A | N/A | N/A | N/A |  |  | 13.3 | 11.4 |  | 3.3 |  | 8446 |  | 8448 |  | T6-WEM01-A |  | TSTWHA01 | EB-STATE4*** | YTHX9421R5101WW | M30 | PREMTBVC1 | T3016US | TCONT824AS52D* | 9825I2 | 564B
kWh to MMBTU |  | Packaged Terminal Air Conditioners | AIRQUEST | Full Service Restaurant | 533 | 801 |  | ≥ 5.4 & < 11.25 Tons | 5.4 | 11.25 | [6 empty] | Geothermal Heat Pumps < 11.25 Tons Closed Loop | 5 | 6 |  | New Construction | [7 empty] | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System Tier 1 | AC611 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC611 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System Room Air Conditioner | 12.1 | 10.6 |  |  | 400 | N/A | 9 | N/A | N/A | Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Single Package | 13.9 | 12.4 |  | 3.4 | 2 | N/A | N/A | N/A | N/A | N/A |  |  | 13.3 | 11.4 |  | 3.3 |  | 8448 |  | 8476 |  | TSTWHA01 |  | TSTWRH01 | EB-STATE5*** | TH8732WFH 5002 | S30 |  | T3017US | ACONT724AS42D* |  | 557
conversion factor |  | Packaged Terminal Heat Pumps | AMANA HEATING AND AIR CONDITIONING | Grocery | 1187 | 186 |  | ≥ 11.25 & < 20 Tons | 11.25 | 20 | [6 empty] | Geothermal Heat Pumps < 11.25 Tons Open Loop | 5 | 6 |  | New Construction | [7 empty] | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System Tier 2 | AC612 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC612 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System Split System | 12.1 | 10.6 |  |  | 400 | 9.5 | 9.3 | N/A | N/A | Air Cooled Heat Pumps ≥ 20 & < 63 Tons Split System | 12.9 | 11.8 |  | 3.3 | 2 | N/A | N/A | N/A | N/A | N/A |  |  | 12.3 | 10.8 |  | 3.2 |  | 8465 |  | 8600 |  | TSTWRH01 |  | SYSTXCCITC01-B |  | TH6320U 2008 | WiFi |  | T3021US | TCONT724AS42D* |  | 563
0.003412 | Ductless Mini-Split Cold Climate Heat Pumps | Cold Climate Air Source Heat Pumps | AMERICAN STANDARD, INC. | High School | 861 | 840 |  | ≥ 20 & < 63 Tons | 20 | 63 | [6 empty] | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) | 5 | 6 |  | New Construction | [7 empty] | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package Tier 0 | AC620 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC620 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System Single Package | 12.1 | 10.6 |  |  | 400 | 9.5 | 9.3 | N/A | N/A | Air Cooled Heat Pumps ≥ 20 & < 63 Tons Single Package | 12.9 | 11.8 |  | 3.3 | 2 | N/A | N/A | N/A | N/A | N/A |  |  | 12.3 | 10.8 |  | 3.2 |  | 8466 |  | 8620 | [5 empty] | TH6320WF 2003 |  |  |  | ACONT624AS42D*
| Cold Climate Air Source Heat Pumps | Ductless Mini-Split Cold Climate Heat Pumps | ARCOAIRE | Hospital | 1424 | 3137 |  | ≥ 20 Tons | 20 | None | [6 empty] | Water Source Heat Pumps < 11.25 Tons All Types | 5 | 4 | Water Source Heat Pump | New Construction |  | Water Source Heat Pump | None |  |  |  |  | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package Tier 1 | AC621 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC621 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Split System Other | 12.1 | 10.6 |  |  | 400 | 9.5 | 9.3 | N/A | N/A | Geothermal Heat Pumps < 11.25 Tons Closed Loop |  | 17 |  | 3.5 | 2 |  | 18 |  | 3.9 | 1500 |  |  |  | 11.2 |  | 3.3 |  | 8476 |  | 8910 | [5 empty] | TH8320R 1003 |  |  |  | TCONT624AS42D*
Displacement | Ductless Multi-Split Cold Climate Heat Pumps | Ductless Multi-Split Cold Climate Heat Pumps | ARMSTRONG AIR CONDITIONING, INC. | Hotel | 3108 | 753 |  | ≥ 63 Tons | 63 | None | [6 empty] | Packaged Terminal Air Conditioners < 0.75 Tons All Types | 2 | 2 | Packaged Terminal Air Conditioner | None |  | Packaged Terminal AC | None |  |  |  |  | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package Tier 2 | AC622 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC622 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package Room Air Conditioner | 12.1 | 10.6 |  |  | 400 | 9.5 | 9.3 | N/A | N/A | Geothermal Heat Pumps < 11.25 Tons Open Loop |  | 20 |  | 4.2 | 2 |  | 23 |  | 4.5 | 1500 |  |  |  | 11.2 |  | 3.3 |  | 8600 |  | 8476W | [5 empty] | TH8321R 1001 |  |  |  | AZON1050AC52Z*
Factor |  |  | BARD MANUFACTURING COMPANY | Large Office | 2250 | 2072 |  | All Sizes | 0 | None | [6 empty] | Packaged Terminal Air Conditioners ≥ 0.75 Tons & < 1 Ton All Types | 2 | 2 | Packaged Terminal Air Conditioner | None |  | Packaged Terminal AC | None |  |  |  |  | Air Conditioners - Air Cooled ≥ 63 Tons Split System Tier 0 | AC710 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC710 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package Split System | 12.1 | 10.6 |  |  | 400 | 9.5 | 9.3 | N/A | N/A | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) |  | 17 |  | 3.5 | 2 |  | 20 |  | 4 | 1500 |  |  |  | 11.2 |  | 3.3 |  | 8620 |  | 8620W | [5 empty] | TH8321WF 1001 |  |  |  | TZON1050AC52Z*
80% |  |  | BEUTLER CORPORATION | Large Retail | 1751 | 2033 | [10 empty] | Packaged Terminal Air Conditioners ≥ 1 Tons All Types | 2 | 2 | Packaged Terminal Air Conditioner | None |  | Packaged Terminal AC | None |  |  |  |  | Air Conditioners - Air Cooled ≥ 63 Tons Split System Tier 1 | AC711 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC711 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package Single Package | 12.1 | 10.6 |  |  | 400 | 9.5 | 9.3 | N/A | N/A | Water Source Heat Pumps < 11.25 Tons All Types |  | 14 |  | 4.6 | 2 | N/A | N/A | N/A | N/A | N/A |  |  |  | 12.2 |  | 4.3 |  | 8910 |  | 8910W | [5 empty] | HZ432K |  |  |  | ACONT850AC52U*
|  |  | BROAN | Light Industrial | 509 | 696 | [10 empty] | Packaged Terminal Heat Pumps < 0.75 Tons All Types | 5 | 4 | Packaged Terminal Air Conditioner | New Construction |  | Packaged Terminal HP | Packaged Terminal AC | None |  |  |  | Air Conditioners - Air Cooled ≥ 63 Tons Split System Tier 2 | AC712 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Split - AC712 | Air Conditioners - Air Cooled ≥ 20 & < 63 Tons Single Package Other | 12.1 | 10.6 |  |  | 400 | 9.5 | 9.3 | N/A | N/A | Packaged Terminal Heat Pumps < 0.75 Tons All Types |  | 12.2 |  | 3.5 | 600 | N/A | N/A | N/A | N/A | N/A |  |  |  | 14 | 3.7 | 0.052 |  | 8476W |  | 8920W | [5 empty] | HZ432 |  |  |  | TCONT850AC52U*
Fossil Fuel Burner |  |  | BRYANT | Motel | 1144 | 604 | [10 empty] | Packaged Terminal Heat Pumps ≥ 0.75 Tons & < 1 Ton All Types | 5 | 4 | Packaged Terminal Air Conditioner | New Construction |  | Packaged Terminal HP | Packaged Terminal AC | None |  |  |  | Air Conditioners - Air Cooled ≥ 63 Tons Single Package Tier 0 | AC720 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC720 | Air Conditioners - Air Cooled ≥ 63 Tons Split System Room Air Conditioner | 11.4 | 10.2 |  |  | 400 | N/A | 8.5 | N/A | N/A | Packaged Terminal Heat Pumps ≥ 0.75 Tons & < 1 Ton All Types |  | 11.4 |  | 3.3 | 600 | N/A | N/A | N/A | N/A | N/A |  |  |  | 14 | 3.7 | 0.052 |  | 8620W |  | 8800
Parasitics (kWh/MMBtu) |  |  | CARRIER AIR CONDITIONING | Primary School | 366 | 819 | [10 empty] | Packaged Terminal Heat Pumps ≥ 1 Tons All Types | 5 | 4 | Packaged Terminal Air Conditioner | New Construction |  | Packaged Terminal HP | Packaged Terminal AC | None |  |  |  | Air Conditioners - Air Cooled ≥ 63 Tons Single Package Tier 1 | AC721 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC721 | Air Conditioners - Air Cooled ≥ 63 Tons Split System Split System | 11.4 | 10.2 |  |  | 400 | N/A | 8.5 | N/A | N/A | Packaged Terminal Heat Pumps ≥ 1 Tons All Types |  | 10.4 |  | 3.1 | 600 | N/A | N/A | N/A | N/A | N/A |  |  |  | 14 | 3.7 | 0.052 |  | 8910W |  | 8810
15 |  |  | COAIRE CORPORATION | Religious | 259 | 704 | [10 empty] | VRF Air Cooled Heat Pumps < 5.4 Tons Multisplit System | 4 | 3 | VRF Air Cooled Heat Pump | New Construction |  | Multisplit System | None |  |  |  |  | Air Conditioners - Air Cooled ≥ 63 Tons Single Package Tier 2 | AC722 | Cooling - HVAC Equipment | Air Conditioners | ACR Air Cooled AC Packaged - AC722 | Air Conditioners - Air Cooled ≥ 63 Tons Split System Single Package | 11.4 | 10.2 |  |  | 400 | N/A | 8.5 | N/A | N/A | VRF Air Cooled Heat Pumps < 5.4 Tons Multisplit System | 15 | 12.5 | 8.5 |  | 2 | 16 | 13 | 9 |  | 230 |  |  | 13 | 11.18 | 7.7 |  |  | 8920W |  | 8820
|  |  | COLEMAN, UNITARY PRODUCTS GROUP | Small Office | 886 | 420 | [10 empty] | VRF Air Cooled Heat Pumps ≥ 5.4 & < 11.25 Tons Multisplit System | 3 | 3 | VRF Air Cooled Heat Pump | New Construction |  | Multisplit System | None |  |  |  |  | Air Conditioners - Water & Evaporatively Cooled All Sizes Split System Tier 1 | AC811 | Cooling - HVAC Equipment | Air Conditioners | ACR Evaporatively Cooled AC Split - AC811 | Air Conditioners - Air Cooled ≥ 63 Tons Split System Other | 11.4 | 10.2 |  |  | 400 | N/A | 8.5 | N/A | N/A | VRF Air Cooled Heat Pumps ≥ 5.4 & < 11.25 Tons Multisplit System | 14.6 | 11.3 |  | 3.4 | 2 | N/A | N/A | N/A | N/A | N/A |  |  | 14.6 | 11 |  | 3.3 |  | 8800 |  | 8830
kW Rounding |  |  | COMFORTMAKER | Small Retail | 818 | 531 | [10 empty] | VRF Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Multisplit System | 3 | 3 | VRF Air Cooled Heat Pump | New Construction |  | Multisplit System | None |  |  |  |  | Air Conditioners - Water & Evaporatively Cooled All Sizes Single Package Tier 1 | AC821 | Cooling - HVAC Equipment | Air Conditioners | ACR Evaporatively Cooled AC Packaged - AC821 | Air Conditioners - Air Cooled ≥ 63 Tons Single Package Room Air Conditioner | 11.4 | 10.2 |  |  | 400 | N/A | 8.5 | N/A | N/A | VRF Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Multisplit System | 13.9 | 10.9 |  | 3.2 | 2 | N/A | N/A | N/A | N/A | N/A |  |  | 13.9 | 10.6 |  | 3.2 |  | 8810 |  | 8840
7 |  |  | CONCORD | University | 1208 | 1104 | [10 empty] | VRF Air Cooled Heat Pumps ≥ 20 Tons Multisplit System | 3 | 3 | VRF Air Cooled Heat Pump | New Construction |  | Multisplit System | None |  |  |  |  | Packaged Terminal Air Conditioners < 0.75 Tons All Types Tier 1 | PTAC101 | Cooling - HVAC Equipment | Air Conditioners | ACR Packaged Termincal AC - PTAC101 | Air Conditioners - Air Cooled ≥ 63 Tons Single Package Split System | 11.4 | 10.2 |  |  | 400 | N/A | 8.5 | N/A | N/A | VRF Air Cooled Heat Pumps ≥ 20 Tons Multisplit System | 12.7 | 10.3 |  | 3.2 | 2 | N/A | N/A | N/A | N/A | N/A |  |  | 12.7 | 9.5 |  | 3.2 |  | 8820
|  |  | DAIKIN AC (AMERICAS), INC. | Warehouse | 371 | 441 | [10 empty] | VRF Water Source Heat Pumps < 11.25 Tons Multisplit System | 5 | 3 | VRF Water Source Heat Pumps | New Construction |  | Multisplit System | None |  |  |  |  | Packaged Terminal Air Conditioners ≥ 0.75 Tons & < 1 Ton All Types Tier 1 | PTAC201 | Cooling - HVAC Equipment | Air Conditioners | ACR Packaged Termincal AC - PTAC201 | Air Conditioners - Air Cooled ≥ 63 Tons Single Package Single Package | 11.4 | 10.2 |  |  | 400 | N/A | 8.5 | N/A | N/A | VRF Water Source Heat Pumps < 11.25 Tons Multisplit System |  | 14 |  | 4.6 | 2 | N/A | N/A | N/A | N/A | N/A |  |  | 16 | 12 |  | 4.3 |  | 8830
kWh Rounding |  |  | DAY & NIGHT | Other | 683 | 664 | [10 empty] | Cold Climate Air Source Heat Pumps All Sizes All Types | 4 | 3 | Split System HP | New Construction |  | Split System AC | Single Package AC | Split System HP | Single Package HP | Other | None | Packaged Terminal Air Conditioners ≥ 1 Tons All Types Tier 1 | PTAC301 | Cooling - HVAC Equipment | Air Conditioners | ACR Packaged Termincal AC - PTAC301 | Air Conditioners - Air Cooled ≥ 63 Tons Single Package Other | 11.4 | 10.2 |  |  | 400 | N/A | 8.5 | N/A | N/A | Cold Climate Air Source Heat Pumps All Sizes All Types | 17 | 11.76 | 10 |  | 2 | N/A | N/A | N/A | N/A | 600 | 750 | 900 | 14 | 11.8 | 8.2 | 2.4033 |  | 8840
5 |  |  | DAYTON ELECTRIC MANUFACTURING COMPANY | [13 empty] | Ductless Multi-Split Cold Climate Heat Pumps All Sizes All Types | 4 | 3 | Ductless Mini-Split HP | New Construction |  | Room Air Conditioner | Ductless Mini-Split AC | Ductless Mini-Split HP | Other | None |  | Geothermal Heat Pumps < 11.25 Tons Closed Loop Tier 0 | GHP100 | Cooling - HVAC Equipment | Heat Pump | ACR Geothermal Heat Pump Closed Loop - GHP100 | Geothermal Heat Pumps < 11.25 Tons Closed Loop Room Air Conditioner |  | 17 |  | 3.5 | 2000 | N/A | 9.5 | N/A | N/A | Ductless Multi-Split Cold Climate Heat Pumps All Sizes All Types | 18 | 11.76 | 10 |  | 2 | N/A | N/A | N/A | N/A | 600 | 750 | 600 | 14 | 11.8 | 8.2 | 2.4033 |  | BCC100 |  | Control Kits- Model Names
|  |  | DIAMONDAIR, INC. | [13 empty] | Ductless Mini-Split Cold Climate Heat Pumps All Sizes All Types | 4 | 3 | Ductless Mini-Split HP | New Construction |  | Room Air Conditioner | Ductless Mini-Split AC | Ductless Mini-Split HP | Other | None |  | Geothermal Heat Pumps < 11.25 Tons Closed Loop Tier 1 | GHP101 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Closed Loop - GHP101 | Geothermal Heat Pumps < 11.25 Tons Closed Loop Split System |  | 17 |  | 3.5 | 2000 | N/A | 9.5 | N/A | N/A | Ductless Mini-Split Cold Climate Heat Pumps All Sizes All Types | 18 | 11.76 | 10 |  | 2 | N/A | N/A | N/A | N/A | 600 | 750 | 600 | 14 | 11.8 | 8.2 | 2.4033 |  | SYSTXBBECC01 |  | Carrier | CMNA ICP-MIDEA | Daikin | EWC Controls | Fujitsu | Gree | Haier | LG Electronics | Mitsubishi Electric | Samsung Electric | Panasonic | Any IR Controlled Mini-split + Flair
MMBTU Rounding |  |  | DUCANE | [25 empty] | Geothermal Heat Pumps < 11.25 Tons Closed Loop Tier 2 | GHP102 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Closed Loop - GHP102 | Geothermal Heat Pumps < 11.25 Tons Closed Loop Single Package |  | 17 |  | 3.5 | 2000 | N/A | 9.5 | N/A | N/A | Integrated control | [9 empty] | 500 | [7 empty] | T6-WEM01-A |  | 24V Interface | 24V Interface | ENVI | Ultra-Zone | Wired Remote Controller (Touch Panel) | Flair Puck + Honeywell T6 Pro Smart | IFTTT | Third Party Tstat Method L Model Series IDU | T-stat Interface + Transformer | Thermostat Adaptor | Honeywell LYRIC | Puck Pro
7 |  |  | EAIR LLC | [25 empty] | Geothermal Heat Pumps < 11.25 Tons Open Loop Tier 0 | GHP200 | Cooling - HVAC Equipment | Heat Pump | ACR Geothermal Heat Pump Open Loop - GHP200 | Geothermal Heat Pumps < 11.25 Tons Closed Loop Other |  | 17 |  | 3.5 | 2000 | N/A | 9.5 | N/A | N/A | [18 empty] | TSTWHA01 | [5 empty] | Novus N2020 |  |  | AUX Heater Kit Highwall Multi | Kumo Station + Kumo Cloud + Outdoor Temperature Sensor |  | Honeywell LYRIC T6
|  |  | ECOTEMP | [25 empty] | Geothermal Heat Pumps < 11.25 Tons Open Loop Tier 1 | GHP201 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Open Loop - GHP201 | Geothermal Heat Pumps < 11.25 Tons Open Loop Room Air Conditioner |  | 20 |  | 4.2 | 2000 | N/A | 9.5 | N/A | N/A | [18 empty] | TSTWRH01 | [5 empty] | Thermostat Converter |  |  | Aux Heater Kit All Ducted/Cassette |  |  | IFTTT Connect
COP to HSPF |  |  | ELECT-AIRE | [25 empty] | Geothermal Heat Pumps < 11.25 Tons Open Loop Tier 2 | GHP202 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Open Loop - GHP202 | Geothermal Heat Pumps < 11.25 Tons Open Loop Split System |  | 20 |  | 4.2 | 2000 | N/A | 9.5 | N/A | N/A | [18 empty] | B36-T10 | [8 empty] | Third Party Tstat Method A Model Series IDU
3.412 |  |  | ENVIROMASTER INTERNATIONAL | [25 empty] | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) Tier 0 | GHP300 | Cooling - HVAC Equipment | Heat Pump | ACR Geothermal Heat Pump Direct Geoexchange - GHP300 | Geothermal Heat Pumps < 11.25 Tons Open Loop Single Package |  | 20 |  | 4.2 | 2000 | N/A | 9.5 | N/A | N/A | [18 empty] | T6-WEM01-A | [8 empty] | A Series IDU Model - Dry Contact Built In
|  |  | EVCON, UNITARY PRODUCTS GROUP | [25 empty] | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) Tier 1 | GHP301 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Direct Geoexchange - GHP301 | Geothermal Heat Pumps < 11.25 Tons Open Loop Other |  | 20 |  | 4.2 | 2000 | N/A | 9.5 | N/A | N/A | [18 empty] | TSTWHA01
|  |  | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP | [25 empty] | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) Tier 2 | GHP302 | Cooling - HVAC Equipment | Heat Pump | Geothermal Heat Pump Direct Geoexchange - GHP302 | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) Room Air Conditioner |  | 17 |  | 3.5 | 2000 | N/A | 9.5 | N/A | N/A | [18 empty] | TSTWRH01 |  | Control Kits- Model Number
|  |  | FRIEDRICH AIR CONDITIONING CO. | [25 empty] | Ductless Mini-Split Heat Pumps < 5.4 Tons All Types Tier 0 | HP100 | Cooling - HVAC Equipment | Heat Pump | ACR Ductless Mini-Split Heat Pump - HP100 | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) Split System |  | 17 |  | 3.5 | 2000 | N/A | 9.5 | N/A | N/A | [18 empty] | SYSTXCCITC01-B |  | Carrier | CMNA ICP-MIDEA | Daikin | EWC Controls | Fujitsu | Gree | Haier | LG Electronics | Mitsubishi Electric | Samsung Electric | Panasonic | Any IR Controlled Mini-split + Flair
Organization Type |  |  | FRIGIDAIRE | [25 empty] | Ductless Mini-Split Heat Pumps < 5.4 Tons All Types Tier 1 | HP101 | Cooling - HVAC Equipment | Heat Pump | ACR Ductless Mini-Split Heat Pump - HP101 | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) Single Package |  | 17 |  | 3.5 | 2000 | N/A | 9.5 | N/A | N/A | [18 empty] | EB-STATE3LT*** | Learning | KSAIC0301230 | KSAIC0401230 | DACA-TSI-1 | BMPlus 3000 | UTY-RNRUZ2 | ICS001P | QAWF01A | PDRYCB300 | PAC-US444CN-1 | TADPT2 | TH8732WFH5002/U | FLAIRPUCK001P
Select… |  |  | FUJITSU GENERAL AMERICA, INC. | [25 empty] | Ductless Mini-Split Heat Pumps < 5.4 Tons All Types Tier 2 | HP102 | Cooling - HVAC Equipment | Heat Pump | ACR Ductless Mini-Split Heat Pump - HP102 | Geothermal Heat Pumps < 11.25 Tons Direct Exchange (DX) Other |  | 17 |  | 3.5 | 2000 | N/A | 9.5 | N/A | N/A | [18 empty] | EB-STATE4*** | Learning |  |  |  | BMPlus 5000 | 8202011300 |  |  | PRARS1 | PAC-WHS01HC-E |  | TH6220WF2006
Government |  |  | GARRISON | [5 empty] | Description | Scenario | a | b | c | d | F cooling | F heating | [12 empty] | Air Cooled Heat Pumps < 5.4 Tons Split System Tier 1 | HP211 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Split - HP211 | [28 empty] | EB-STATE5*** | Learning |  |  |  | BMPlus 7000 | UTY-TTRX |  |  | PRARH0 | C7089U1006/U |  | PICDF19
Not Incorporated |  |  | GD MIDEA AIR-CONDITIONING EQUIPMENT CO., LTD. | [5 empty] | Cold Climate Air Source Heat Pumps Separate Control 0.5 | 4a | 0.26 | 1.068 | -9.59 | 1.29 | 0.98 | 0.52 | [12 empty] | Air Cooled Heat Pumps < 5.4 Tons Split System Tier 2 | HP212 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Split - HP212 | [28 empty] | YTHX9421R5085WW | Connected |  |  |  | UZC-4 |  |  |  | IDU MODEL | PAC-USWHS002-WF-1
Incorporated |  |  | GE CONSUMER & INDUSTRIAL | [5 empty] | Cold Climate Air Source Heat Pumps Separate Control 0.7 | 4b | 0.145 | 1.086 | -11.85 | 1.424 | 1 | 0.67 | [12 empty] | Air Cooled Heat Pumps < 5.4 Tons Single Package Tier 1 | HP221 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Packaged - HP221 | [28 empty] | YTHX9421R5101WW | Connected |  |  |  | UZC-6 |  |  |  |  | VPL24-210
|  |  | GRANDAIRE | [5 empty] | Ductless Mini-Split Cold Climate Heat Pumps Separate Control 0.3 | 2a | 2.38 | 0.338 | 11.07 | 0.165 | 0.91 | 0.37 | [12 empty] | Air Cooled Heat Pumps ≥ 5.4 & < 11.25 tons Single Package Tier 1 | HP321 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Packaged - HP321 | [28 empty] | TH6320WF 2003 | Learning
Building Type |  |  | GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | [5 empty] | Ductless Mini-Split Cold Climate Heat Pumps Separate Control 0.5 | 2b | 2.506 | 0.296 | 10.08 | 0.277 | 0.99 | 0.55 | [12 empty] | Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Split System Tier 1 | HP411 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Split - HP411 | [5 empty] | * ($/Ton) | [22 empty] | TH8320R 1003
[9 empty] | Ductless Mini-Split Cold Climate Heat Pumps Separate Control 0.7 | 2c | 2.768 | 0.21 | 9.44 | 0.323 | 1 | 0.76
[9 empty] | Ductless Multi-Split Cold Climate Heat Pumps Separate Control 0.7 | 3a | -3.793 | 2.217 | 11.6 | 0.196 | 1 | 0.86
Select… |  |  | GUANGDONG CHIGO AIR-CONDITIONING CO., LTD. | [25 empty] | Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Single Package Tier 1 | HP421 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Packaged - HP421 | [28 empty] | TH8321R 1001
College |  |  | GUARDIAN, UNITARY PRODUCTS GROUP | [5 empty] | Source: Updated per 2024 PSEG Long Island TRM (NYS TRM V10) | [19 empty] | Air Cooled Heat Pumps ≥ 20 & < 63 Tons Split System Tier 1 | HP511 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Split - HP511 | [28 empty] | TH8321WF 1001 | Connected
Grocery |  |  | HAIER AMERICA | [25 empty] | Air Cooled Heat Pumps ≥ 20 & < 63 Tons Single Package Tier 1 | HP521 | Cooling - HVAC Equipment | Heat Pump | ACR Air Cooled Heat Pump Packaged - HP521 | [28 empty] | E30
Health |  |  | HEAT CONTROLLER, INC. | [25 empty] | Water Source Heat Pumps < 11.25 Tons All Types Tier 1 | HP601 | Cooling - HVAC Equipment | Heat Pump | ACR Water Source Heat Pump - HP601 | [28 empty] | M30
Hospital |  |  | HEIL | [25 empty] | Packaged Terminal Heat Pumps < 0.75 Tons All Types Tier 1 | PTHP101 | Cooling - HVAC Equipment | Heat Pump | ACR Packaged Terminal Heat Pump - PTHP101 | [28 empty] | S30
Hotel |  |  | ICP COMMERCIAL | [25 empty] | Packaged Terminal Heat Pumps ≥ 0.75 Tons & < 1 Ton All Types Tier 1 | PTHP201 | Cooling - HVAC Equipment | Heat Pump | ACR Packaged Terminal Heat Pump - PTHP201 | [28 empty] | WiFi
Manufacturing |  |  | INNOVAIR CORPORATION | [25 empty] | Packaged Terminal Heat Pumps ≥ 1 Tons All Types Tier 1 | PTHP301 | Cooling - HVAC Equipment | Heat Pump | ACR Packaged Terminal Heat Pump - PTHP301 | [28 empty] | PREMTVBC0
Office |  |  | INTERNATIONAL REFRIGERATION PRODUCTS, INC. | [25 empty] | VRF Air Cooled Heat Pumps < 5.4 Tons Multisplit System Tier 1 | VHP211 | Cooling - HVAC Equipment | Heat Pump | VRF Water Source Heat Pump - VHP211 | [28 empty] | PREMTBVC1
Retail |  |  | INTERTHERM | [25 empty] | VRF Air Cooled Heat Pumps < 5.4 Tons Multisplit System Tier 2 | VHP212 | Cooling - HVAC Equipment | Heat Pump | VRF Air Cooled Heat Pump - VHP212 | [28 empty] | T3008US | Learning
Restaurant |  |  | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | [25 empty] | VRF Air Cooled Heat Pumps ≥ 5.4 & < 11.25 Tons Multisplit System Tier 1 | VHP311 | Cooling - HVAC Equipment | Heat Pump | VRF Air Cooled Heat Pump - VHP311 | [28 empty] | T3016US | Learning
Religious |  |  | KEEPRITE | [25 empty] | VRF Air Cooled Heat Pumps ≥ 11.25 & < 20 Tons Multisplit System Tier 1 | VHP321 | Cooling - HVAC Equipment | Heat Pump | VRF Air Cooled Heat Pump - VHP321 | [28 empty] | T3017US | Learning
School |  |  | KELVINATOR | [25 empty] | VRF Air Cooled Heat Pumps ≥ 20 Tons Multisplit System Tier 1 | VHP411 | Cooling - HVAC Equipment | Heat Pump | VRF Air Cooled Heat Pump - VHP411 | [28 empty] | T3021US | Learning
Warehouse |  |  | KENMORE | [25 empty] | VRF Water Source Heat Pumps < 11.25 Tons Multisplit System Tier 1 | VHP421 | Cooling - HVAC Equipment | Heat Pump | VRF Air Cooled Heat Pump - VHP421 | [28 empty] | ACONT824AS52D*
Other |  |  | KLIMAIRE PRODUCTS INC. | [25 empty] | Ductless Mini-Split Cold Climate Heat Pumps All Sizes All Types | CCHP101 | Cooling - HVAC Equipment | Heat Pump | Ductless Mini-Split Cold Climate Heat Pump - CCHP101
|  |  | LENNOX INDUSTRIES, INC. | [25 empty] | Ductless Mini-Split Cold Climate Heat Pumps All Sizes All Types New Construction | CCHP101-NC | Cooling - HVAC Equipment | Heat Pump | Ductless Mini-Split Cold Climate Heat Pump - CCHP101-NC
Project Type |  |  | LG ELECTRONICS, INC. | [5 empty] | HSPF Climate Adjustment Factor | [19 empty] | Ductless Mini-Split Cold Climate Heat Pumps All Sizes All Types Existing Oil NO CAC | CCHP101-OC | Cooling - HVAC Equipment | Heat Pump | Ductless Mini-Split Cold Climate Heat Pump - CCHP101-OC
Select… |  |  | LUXAIRE, UNITARY PRODUCTS GROUP | [5 empty] | HSPF <8.5 | 0.8 | [18 empty] | Ductless Mini-Split Cold Climate Heat Pumps All Sizes All Types All Other | CCHP101-AO | Cooling - HVAC Equipment | Heat Pump | Ductless Mini-Split Cold Climate Heat Pump - CCHP101-AO
New Construction |  |  | MAMMOTH, INC. | [5 empty] | HSPF >8.5 | 0.78 | [18 empty] | Ductless Multi-Split Cold Climate Heat Pumps All Sizes All Types | CCHP151 | Cooling - HVAC Equipment | Heat Pump | Ductless Multi-Split Cold Climate Heat Pump - CCHP151
Existing Building |  |  | MARATHERM | [25 empty] | Ductless Multi-Split Cold Climate Heat Pumps All Sizes All Types New Construction | CCHP151-NC | Cooling - HVAC Equipment | Heat Pump | Ductless Multi-Split Cold Climate Heat Pump - CCHP151-NC
|  |  | MAYTAG | [25 empty] | Ductless Multi-Split Cold Climate Heat Pumps All Sizes All Types Existing Oil NO CAC | CCHP151-OC | Cooling - HVAC Equipment | Heat Pump | Ductless Multi-Split Cold Climate Heat Pump - CCHP151-OC
Rebate Payment Method |  |  | MCQUAY INTERNATIONAL | [25 empty] | Ductless Multi-Split Cold Climate Heat Pumps All Sizes All Types All Other | CCHP151-AO | Cooling - HVAC Equipment | Heat Pump | Ductless Multi-Split Cold Climate Heat Pump - CCHP151-AO
Select… | [28 empty] | Cold Climate Air Source Heat Pumps All Sizes All Types | CCHP211 | Cooling - HVAC Equipment | Heat Pump | Ducted Cold Climate Heat Pump - CCHP211
Check to Customer | [28 empty] | Cold Climate Air Source Heat Pumps All Sizes All Types New Construction | CCHP211-NC | Cooling - HVAC Equipment | Heat Pump | Ducted Cold Climate Heat Pump - CCHP211-NC
Assigned to Contractor | [28 empty] | Cold Climate Air Source Heat Pumps All Sizes All Types Existing Oil No CAC | CCHP211-OC | Cooling - HVAC Equipment | Heat Pump | Ducted Cold Climate Heat Pump - CCHP211-OC
|  |  | MEDALLION | [25 empty] | Cold Climate Air Source Heat Pumps All Sizes All Types All Other | CCHP211-AO | Cooling - HVAC Equipment | Heat Pump | Ducted Cold Climate Heat Pump - CCHP211-AO
|  |  | MILLER | [25 empty] | Integrated/Modulating Control | CEP405 | Cooling - HVAC Equipment | Cooling & Controls | Cooling HVAC Equipment - CEP405
|  |  | MITSUBISHI ELECTRIC AND ELECTRONICS USA, INC. | [25 empty] | Integrated/Fixed Capacity Control | CEP406 | Cooling - HVAC Equipment | Cooling & Controls | Cooling HVAC Equipment - CEP406
|  |  | NATIONAL COMFORT PRODUCTS | [25 empty] | Dual Fuel Thermostat | CEP410 | Cooling - HVAC Equipment | Cooling & Controls | Cooling HVAC Equipment - CEP410
DAC |  |  | NORDYNE, INC. | [25 empty] | Integrated Controls | CEP402 | Cooling - HVAC Equipment | Cooling & Controls | Cooling HVAC Equipment - CEP402
Select… |  |  | NUTONE
Yes |  |  | PANASONIC CORPORATION OF NORTH AMERICA
No |  |  | PAYNE HEATING AND COOLING
Unsure |  |  | PETRA ENGINEERING INDUSTRIES CO.
PHILCO
QUIETSIDE
RHEEM MANUFACTURING COMPANY
RICHMOND
RUUD AIR CONDITIONING DIVISION
SANYO COMMERCIAL SOLUTIONS
TAPPAN
TEMPSTAR
TEXAS FURNACE, LLC
THERMO PRODUCTS, INC.
TRANE
UNITED REFRIGERATION DISTRIBUTORS, INC.
V-AIRE
WEATHERKING AIR CONDITIONING DIVISION
WESTINGHOUSE
WHIRLPOOL
XENON
YMGI GROUP LLC.
YORK, UNITARY PRODUCTS GROUP
OTHER
*ODC TRM kWh value
| Equipment Type (Existing) | Coincidence Factor | Free Ridership | Spillover* | Line Loss kW Summer | Line Loss kWh | In-Servce Rate
| Room Air Conditioners | 0.3 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Ductless Mini-Split AC | 0.45 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Air Conditioners - Air Cooled | 0.57 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Air Conditioners - Water & Evaporatively Cooled | 0.57 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Packaged Terminal Air Conditioners | 0.45 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Ductless Mini-Split Heat Pumps | 0.45 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Air Cooled Heat Pumps | 0.57 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Water Source Heat Pumps | 0.45 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Geothermal Heat Pumps | 0.57 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Packaged Terminal Heat Pumps | 0.45 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| VRF Air Cooled Heat Pumps | 0.57 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| VRF Water Source Heat Pumps | 0.45 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Cold Climate Air Source Heat Pumps | 0.45 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Ductless Mini-Split Cold Climate Heat Pumps | 0.45 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Ductless Multi-Split Cold Climate Heat Pumps | 0.45 | 0.3 | 0.0155 | 0.0719 | 0.0567 | 1
| Integrated Control | 0 | 0 | 0 | 0 | 0 | 0
| Existing Heat | Baseline Efficiency | lbs CO2/unit | 2204.6
| Existing Gas | 80% | 117.1304 | 0.05313
| Existing Oil | 82% | 163.0522 | 0.07396
| Existing Propane | 80% | 135.7813 | 0.05313
| Baseline New Construction | 80% | 117.1304
| Existing Electric |  | 1.1962 | kWh
| Existing Other |  | 1.1962
| Baseline None | NA | 1.1962
NA
Ventilation Measure
Drop Down List
| Equipment Type (Existing Unit) | Heating Fuels (Existing) | Equipment Type (New Unit) | Fan Type | Building Construction Type | Size Category
| Air Conditioners - Air Cooled | Electric | Energy Recovery Ventilator (ERV) | 16 Feet HVLS | Existing Building | < 5.4 Tons
| Air Conditioners - Water Cooled | Gas | Heat Recovery Ventilator (HRV) | 17 Feet HVLS | New Construction | ≥ 5.4 & < 11.25 Tons
| Make-Up Air Unit | Oil |  | 18 Feet HVLS |  | ≥ 11.25 & < 20 Tons
|  | Propane |  | 19 Feet HVLS |  | ≥ 20 & < 63 Tons
|  | Other |  | 20 Feet HVLS
|  | None |  | 21 Feet HVLS
22 Feet HVLS
23 Feet HVLS
24 Feet HVLS
Default Values (ERV/HRV Measure) All values from NY TRM V10
| H Outdoor Cooling | 30.86 | Btu/lb | Defaults Values (HVLS Fans)
| H Indoor Cooling | 25.3 | Btu/lb | Operating Hours | 4988 |  | Existing Fan Type | lbf/kW
| T Indoor Heating | 70 | F | CFM/Watts | 15 | New Construction/If unknown | 24" - 35" Diameter | 10.5
| T Outdoor Heating | 53.2 | F | CF | 0.8 | CF | 36" - 47" Diameter | 12.9
| T Outdoor Cooling | 73.69 | F | Units | 5 | New Construction/If unknown | 48" - 52" Diameter | 19.8
| T Indoor Cooling | 70 | F | Conversion factor, one kW equals 1,000 Watts | 1000 |  | 53" + | 20.8
| Fan Efficiency | 67% |  |  |  |  | Average | 16
| Fan Motor Efficiency | 70%
| CF | 0.8 |  |  |  |  | VFD | FVFD,EE
|  |  |  | NYS TRM V10 (NYC) |  |  | Yes | 0.75
| Existing Equipment (Air Conditioner Air Cooled Package Unit) |  |  | Operating Days | Cooling | Heating | No | 1
| Size Category | Seer/IEER |  | 24/7 - 365 | 2684 | 5920
| < 5.4 Tons | 14 | SEER | Mon - Sun 6AM-12AM | 2152 | 4303
| ≥ 5.4 & < 11.25 Tons | 12.7 | IEER | Mon - Sun 6AM-10PM | 1946 | 3796
| ≥ 11.25 & < 20 Tons | 12.2 | IEER | Mon - Fri 7AM-7PM and Sun 11AM-6PM | 1220 | 2204
| ≥ 20 & < 63 Tons | 11.4 | IEER | Mon - Fri 7AM-7PM | 1081 | 1984
|  |  |  | Mon - Fri 7AM-5PM | 890 | 1663
| Existing Equipment (Air Conditioner Water Cooled Package Unit) |  |  | Other | 1662 | 3312 | Avg values
| Size Category | Seer/IEER
| < 5.4 Tons | 12.3 | SEER
| ≥ 5.4 & < 11.25 Tons | 13.7 | IEER
| ≥ 11.25 & < 20 Tons | 13.7 | IEER
| ≥ 20 & < 63 Tons | 13.4 | IEER
| Existing Heating Equipment | Efficiency
| Existing Gas | 80%
| Existing Oil | 82%
| Existing Propane | 80%
| Existing Electric | 3.412 | HSPF
| Equipment Type (Existing Unit) | SEER/IEER (ASHRAE 90.1 2016)
| Air Conditioners - Air Cooled < 5.4 Tons | 14
| Air Conditioners - Air Cooled ≥ 5.4 & < 11.25 Tons | 12.7
| Air Conditioners - Air Cooled ≥ 11.25 & < 20 Tons | 12.2
| Air Conditioners - Air Cooled ≥ 20 & < 63 Tons | 11.4
| Air Conditioners - Water Cooled < 5.4 Tons | 12.3
| Air Conditioners - Water Cooled ≥ 5.4 & < 11.25 Tons | 13.7
| Air Conditioners - Water Cooled ≥ 11.25 & < 20 Tons | 13.7
| Air Conditioners - Water Cooled ≥ 20 & < 63 Tons | 13.4
| Make-Up Air Unit < 5.4 Tons | 14
| Make-Up Air Unit ≥ 5.4 & < 11.25 Tons | 12.7
| Make-Up Air Unit ≥ 11.25 & < 20 Tons | 12.2
| Make-Up Air Unit ≥ 20 & < 63 Tons | 11.4
Conversion
| 4.5 | Density of inlet air at 70ºF x 60 min/hr, in lb-min/ft3-hr
| 1.08 | Specific heat of air × density of inlet air @ 70°F × 60 min/hr in BTU/h-ºF CFM
| 1000000 | Conversion factor, one MMBtu equals 1,000,000 BTU
| 33013 | Conversion factor from horsepower to ft.lb/min
| 5.202 | Conversion factor from inches of water to pounds per square ft (lb/sq.ft.)
| 0.746 | Conversion factor (kW/hp), 746 watts equals one electric horsepower
| 1000 | Conversion factor, one kW equals 1,000 Watts
Rebate
| ERV Rebate | 70 | $/100CFM
| HRV Rebate | 60 | $/100CFM
Rebate
| Fan Type | Rebate ($50/Diameter) | Feet
| 16 Feet HVLS | 800 | 16
| 17 Feet HVLS | 850 | 17
| 18 Feet HVLS | 900 | 18
| 19 Feet HVLS | 950 | 19
| 20 Feet HVLS | 1000 | 20
| 21 Feet HVLS | 1050 | 21
| 22 Feet HVLS | 1100 | 22
| 23 Feet HVLS | 1150 | 23
| 24 Feet HVLS | 1200 | 24

## CEE Comparison (hidden)
Equipment Type | Size Category | Subcategory | CEE Tier 0 | Current LIPA Existing Equip. | CEE Tier 1 | Current LIPA New Equip. | CEE Tier 2 | Tier 1 | Tier 2 | Comments
Air conditioners, Air cooled (Cooling Mode) | < 5.4 Tons | Split System | NA | 14.0 SEER 12.0 EER | 14.0 SEER 12.0 EER | 15.0 SEER 12.5 EER | 15.0 SEER 12.5 EER | No Change | No Change
|  | Single Package | NA | 14.0 SEER 11.6 EER | 14.0 SEER 11.6 EER | 15.0 SEER 12.0 EER | 15.0 SEER 12.0 EER | No Change | No Change
| ≥ 5.4 & < 11.25 Tons | Split System | 11.7 EER | 11.5 EER | 11.5 EER | 12.0 EER | 12.0 EER | No Change | No Change
|  | Single Package | 11.6 IEER | 11.5 EER | 12.8 IEER | 12.0 EER | 13.8 IEER | Change | Change | IEER added to criteria; efficiency ratings do not differentiate between Split or Single
| ≥ 11.25 & < 20 Tons | Split System | 11.5 EER | 11.5 EER | 11.5 EER | 12.0 EER | 12.0 EER | No Change | No Change
|  | Single Package | 11.6 IEER | 11.5 EER | 12.3 IEER | 12.0 EER | 13.0 IEER | Change | Change | IEER added to criteria; efficiency ratings do not differentiate between Split or Single
| ≥ 20 & < 63 Tons | Split System | 10.3 EER | 10.5 EER | 10.3 EER | 10.8 EER | 10.6 EER | Change | Change | Change in EER
|  | Single Package | 10.4 IEER | 10.5 EER | 11.1 IEER | 10.8 EER | 12.1 IEER | Change | Change | IEER added to criteria; efficiency ratings do not differentiate between Split or Single
| ≥ 63 Tons | Split System | 9.7 EER | 9.7 EER | 9.7 EER | 10.2 EER | 10.2 EER | No Change | No Change
|  | Single Package | 9.8 IEER | 9.7 EER | 10.9 IEER | 10.2 EER | 11.4 IEER | Change | Change | IEER added to criteria; efficiency ratings do not differentiate between Split or Single
Air Conditioners, Water and Evaporatively Cooled | All Sizes | Split System | NA | 14 EER | NA | NA | NA
|  | Single Package | NA | 14 EER | NA | NA | NA
Air Conditioners, Water Cooled | < 5.4 Tons | Split System | NA | NA | 14 EER | NA | NA
|  | Single Package | NA | NA | 14 EER | NA | NA
| ≥ 5.4 & < 11.25 Tons | Split System | NA | NA | 13.8 EER | NA | NA
|  | Single Package | NA | NA | 15.1 IEER | NA | NA
| >=11.25 Tons | Split System | NA | NA | 13.8 EER | NA | NA
|  | Single Package | NA | NA | 14.6 IEER | NA | NA
Air Conditioners, Evaporatively Cooled | < 5.4 Tons | Split System | NA | NA | 14 EER | NA | NA
|  | Single Package | NA | NA | 14 EER | NA | NA
| ≥ 5.4 & < 11.25 Tons | Split System | NA | NA | 13.8 EER | NA | NA
|  | Single Package | NA | NA | 15.1 IEER | NA | NA
| >=11.25 Tons | Split System | NA | NA | 13.3 EER | NA | NA
|  | Single Package | NA | NA | 14.1 IEER | NA | NA
Equipment Type | Size Category | Subcategory | CEE Tier 0 (Cooling Mode) | Current LIPA Existing Equip. | CEE Tier 1 | Current LIPA New Equip. | CEE Tier 2
Air Cooled Heat Pumps | < 5.4 Tons | Split System |  | NA | 14.0 SEER 12.0 EER 8.5 HSPF | 14.0 SEER 12.0 EER 8.5 HSPF | 15.0 SEER 12.5 EER 9.0 HSPF | No Change
|  | Single Package |  | NA | 14.0 SEER 11.6 EER 8.0 HSPF | 14.0 SEER 11.6 EER 8.0 HSPF | 15.0 SEER 12.0 EER 8.5 HSPF | No Change
| ≥ 5.4 & <11.25 tons | Split System | 11.1 EER | NA | 11.1 EER 12.1 IEER 3.4 COP | 11.5 EER 3.4 COP | NA | Change |  | Change in EER
|  | Single Package | 11.2 IEER | NA |  | 11.5 EER 3.4 COP | NA | Change |  | IEER added to criteria; efficiency ratings do not differentiate between Split or Single
| ≥ 11.25 & < 20 Tons | Split System | 10.7 EER | NA | 10.7 EER 11.7 IEER 3.2 COP | 11.5 EER 3.2 COP | NA | Change |  | Change in EER
|  | Single Package | 10.8 IEER | NA |  | 11.5 EER 3.2 COP | NA | Change |  | IEER added to criteria; efficiency ratings do not differentiate between Split or Single
| ≥ 20 & < 63 Tons | Split System | 10.1 EER | NA | 10.1 EER 10.7 IEER 3.2 COP | 10.5 EER 3.2 COP | NA | Change |  | Change in EER
|  | Single Package | 10.2 IEER | NA |  | 10.5 EER 3.2 COP | NA | Change |  | IEER added to criteria; efficiency ratings do not differentiate between Split or Single
Water Source Heat Pumps | < 11.25 Tons | N/A | No Spec. | NA | 14.0 EER 4.6 COP | 14.0 EER 4.6 COP | NA | No Change
Equipment Type | Size Category | Subcategory | CEE Tier 0 (Cooling Mode) | Current LIPA Existing Equip. | CEE Tier 1 | Current LIPA New Equip. | CEE Tier 2
VRF Air Cooled (Cooling Mode) | < 5.4 Tons | Split System | NA | 14.0 SEER 12.0 EER | 14.0 SEER 12.0 EER | 15.0 SEER 12.5 EER | 15.0 SEER 12.5 EER | No Change | Change
|  | Single Package | NA | 14.0 SEER 11.6 EER | NA | 15.0 SEER 12.0 EER | NA | Change | Change
| ≥ 5.4 & < 11.25 Tons | Split System | 11.7 EER | 11.5 EER | 11.7 EER | 12.0 EER | NA | Change | Change | Change in EER
|  | Single Package | 11.6 IEER | 11.5 EER | 14.9 IEER | 12.0 EER |  | Change | Change | IEER added to criteria; efficiency ratings for "Multisplit system"
| ≥ 11.25 & < 20 Tons | Split System | 11.5 EER | 11.5 EER | 11.7 EER | 12.0 EER | NA | Change | Change | Change in EER
|  | Single Package | 11.6 IEER | 11.5 EER | 14.4 IEER | 12.0 EER |  | Change | Change | IEER added to criteria; efficiency ratings for "Multisplit system"
| ≥ 20 & < 63 Tons | Split System | 10.3 EER | 10.5 EER | 10.5 EER | 10.8 EER | NA | No Change | Change
|  | Single Package | 10.4 IEER | 10.5 EER | 13.0 IEER | 10.8 EER |  | Change | Change | IEER added to criteria; efficiency ratings for "Multisplit system"